#### Ministry of Water and Energy (MEW)

Technical Specification

FOR

DESIGN-BUILD FOR ELECTRIFICATION OF QUSH TEPA & DARZAAB DISTRICTS

Qushtepa and Darzaab 220/20 Kv substations

IN

JOZJAN PROVINCE

July, 2026

Contents

Chapter 01	13

Scope of Supply of Plant and Services	13

1. General Information:	14

1.1. Project Location:	15

1.2 Climate and Geographic Condition:	15

2. SCOPE OF SUPPLY AND SERVICES FOR 220/20 kV QUSHTEPA AND DARZAAB SUBSTATIONS	17

2.1 General Requirements	17

2.2 Detailed Engineering and Design	19

2.3 220 kV Outdoor Switchyard	21

2.4 20 kV Metal-Clad Switchgear	23

2.5 220/20 kV Power Transformer System	23

2.6 Transformer Protection and Control	24

2.7 Control and Protection Systems	25

2.8 220 kV Busbar Protection System	25

2.9 220 kV Transmission-Line Protection and Control	26

2.10 20 kV Protection and Control	26

2.11 Substation Automation System, SCADA, and RTU	27

2.12 AC Auxiliary Power System	27

2.13 DC Battery and Charger System	28

2.14 UPS System	28

2.15 Cable Systems	28

2.16 Earthing and Lightning-Protection Systems	28

2.17 Indoor and Outdoor Lighting	29

2.18 Fire Detection and Fire Protection	29

2.19 CCTV, Security, and Access-Control Systems	30

2.20 Testing, Commissioning, Energization, and Trial Operation	30

2.21 Training	31

2.22 Employer Participation in Factory Acceptance Tests	31

2.23 Testing and Measuring Facilities	31

2.24 Transportation, Delivery, Handling, and Storage	32

2.25 Mandatory Spare Parts and Special Tools	32

2.26 Documentation	32

2.27 Limits of Supply and Interfaces	33

Chapter 02	34

General Project Requirements and Documentation	34

1. General	36

2. Bidding Stage	36

3. Contracting Stage	37

3.1 Detailed Design and Manufacturing Stage	37

General	37

3.2 Identification on Drawings	38

3.3 Requirements	38

3.4 Time Schedules, Work Programs	39

3.5 Electrical Engineering	40

3.6 Control and Protection System Engineering	40

3.7 Erection Stage	41

3.8 Documentation for Final Erection Checks	41

3.9 As-Built Drawings and Documents	42

3.10 Commissioning Documentation	43

3.11 Documentation for Taking Over	43

3.12 Operation and Maintenance Instructions, Manuals	43

Arrangement	45

3.13 Documents Preparation and Submission	46

3.14 Drawings and Documents Approval Procedure	51

3.15 Correspondence	56

General	56

4. Project Control and Reporting	57

4.1 Reporting	57

4.2 Meetings	60

5. Handing Over of Documents, Goods and Materials	61

6. Computer Hardware and Software	62

7. Surplus Construction Material	62

7.1 Cable Scrap and Surplus Material	62

7.2 Packing Material	62

8. Health, Safety and Environmental Matters	62

8.1 HSE (Health, Safety and Environment) Management Plan	62

8.2 Land Acquisition and Resettlement	63

Chapter 03	64

General Technical Requirements	64

1. General Technical Requirements	66

1.1 General	66

1.2 Standards and codes of practice	66

1.3 Units of measurement	67

1.4 Health, Safety and Environmental	70

1.5 Environmental Protection Plan	70

1.6 Signs	71

1.7 Quality Assurance	71

1.8 Corrosion protection and painting	73

1.9 General Requirements for Galvanizing	77

1.10 Standardization of makes	78

1.11 Fire protection for materials and for building elements	79

1.12 Installation	80

1.13 Steel structures and assembly material	80

2. General Electrical Requirements	81

2.1 General	81

2.2 Voltage levels used in the system	81

2.3 Protection class for electrical operational equipment	81

2.4 Electrical protective measures	82

2.5 Protective measures for installations up to 1000 V	82

2.6 Protective measures for installations over 1000 V	82

2.7 Requirements for local control cubicles and housing for switchgear, control, measurement and signaling equipment	86

2.8 Terminal boxes and terminal cabinets	88

2.9 Power, control and measuring cables and cable supporting structures	88

2.10 Cable supporting structures	91

2.11 General Requirements for control and monitoring equipment	92

2.12 Power supplies and fusing	94

2.13 Indicators	95

2.14 Switches and relays	95

2.15 Measurement of electrical parameters	95

2.16 Wiring, cabling terminals	96

2.17 Labeling and scales	96

2.18 Diagrams, lists and charts	96

2.20 Cable schedule, cable list	97

3. General Requirements Civil Works	98

3.1 Site Construction Works	98

4. Inspection and testing of the 220/20 kV Qush Tepa and Darzaab Substations	100

4.1 General	100

4.2 Scope, program, documentation	101

4.3 Applicable standards for inspection and testing	103

4.4 Test equipment and instruments	104

4.5 Independent agency	104

4.6 Type Tests	104

4.7 Inspections and Tests during Manufacture	105

4.8 Test and inspection of materials	106

4.9 Welding and surface coating tests	107

4.10 Primary electrical equipment	107

4.11 Control and monitoring equipment	108

4.12 Telecommunication equipment	110

4.14 Inspection and testing during erection for the substations	111

4.15 Tests on completion for the substations	112

Chapter 04	114

220 kV Outdoor Switchyard	114

1. 220 kV Outdoor Switchyard	115

1.1 General	115

1.2 Equipment supports, gantries and other steel constructions	115

1.3 Bus bars	116

1.4 Equipment connections	116

1.5 Overhead conductors	117

1.6 Ground wires	117

1.7 Post insulators	118

1.8 Insulator units, string insulators	118

Proof of compliance	118

1.9 Circuit breaker	119

1.10 Isolators and earthing switches	120

1.11 Voltage transformer	120

1.12 Current transformer	121

1.13 Surge arresters	122

Chapter 05	123

220/20 kV Power Transformer	123

1. Power Transformer	124

1.1 General	124

1.2 Power transformer	124

1.3 Technical Requirements for the Power Transformer	124

Chapter 06	128

20 kV MV Switchgear	128

1. 20 kV Switchgear	129

1.1 General	129

1.2 Switchgear components	129

Chapter 07	132

MV and Low Voltage Cables	132

1. MV and LV Cables and Cable Support Structures	133

1.1 General	133

1.2 Technical requirements	133

Chapter 08	137

AC and DC Installations	137

1. AC DC Supply and Installations	138

1.1 General	138

1.2 Technical Requirements	138

Chapter 09	142

Lighting and Small Power Installation	142

Qush Tepa 220/20 kV Substation and Darzaab 220/20 kV Substation	142

1. Lighting and Small Power Installation	143

1.1 General	143

1.2 Technical Requirements	143

Chapter 10	147

Earthing System and Lightning Protection	147

Qush Tepa 220/20 kV Substation and Darzaab 220/20 kV Substation	147

1. Earthing System and Lightning Protection	148

1.1 General	148

1.2 Technical Requirements	148

Chapter 11	152

220 kV and 20 kV Protection including Test Requirements for Qush Tepa and Darzaab Substations	152

Qush Tepa 220/20 kV Substation and Darzaab 220/20 kV Substation	152

1. Current and Voltage Transformer Requirements	153

2. Auto-reclosing Concept in the Qush Tepa and Darzaab Substations	153

3. References	153

4. Housing, Wiring, Identification	154

5. Testing Facilities, Indications	154

6. Auxiliary Supply	155

7. Tripping Circuits	155

8. Electromagnetic Interference, Insulation	156

9. Quality Assurance	156

10. Main Equipment Design for Protection and Control Equipment	157

10.1 Serial Interfacing of Relays	157

10.2 Line Differential Protection Including Auto-reclosing	158

10.3 Distance Protection (Function) Including Auto-Reclosing	160

10.4 Time-Overcurrent Functions	161

10.5 Directional Earth Fault Functions	162

10.6 Overvoltage Protection Functions	162

10.7 Under Voltage Protection Functions	162

10.8 Circuit Breaker Failure Protection	162

10.9 Under- and Over Frequency Protection Functions	163

10.10 Synchro-check Function	163

10.11 Overload Protection with Thermal Replica	163

10.12 Protection Settings Report	163

Chapter 12	165

Qush Tepa and Darzaab Substations SCADA and Communication System	165

Qush Tepa 220/20 kV Substation and Darzaab 220/20 kV Substation	165

RTU Requirements & Specifications	166

1. Brief Description	166

2. General Requirements	166

3. Technical Requirements	167

Telecommunication Requirements & Specifications	167

1. Telecommunication through Fiber Optic (SDH & DWDM with OTN)	167

1.1 Scope	167

1.2 General Features	167

2. Teleprotection – Tele-protection of Power Transmission Lines	168

3. PABX	168

4. VHF for Communication between Switchyards & Local Control Centers Maintenance Works	168

2.  SCADA / REMOTE TERMINAL UNIT (RTU) REQUIREMENTS	168

2.1  General Requirements	168

2.2  Technical Requirements	168

2.3  Communication Ports	170

2.4  Power Coupler	172

2.5  Opto-Isolated Control Inputs	172

2.6  Abbreviations	174

3.  TELECOMMUNICATION REQUIREMENTS & SPECIFICATIONS	177

3.1  Telecommunication through Fiber Optic (SDH & DWDM with OTN)	177

3.2  Teleprotection of Power Transmission Lines	181

3.3  PABX Exchange / Telephony System	184

3.4  VHF for Communication between Switchyards and Local Control Centers	186

4.  POWER QUALITY METER (PQM)	187

4.1  Brief Description	187

4.2  General Requirements	187

4.3  Measurement and Recording Capability	188

4.4  Environmental and Electromagnetic Compatibility	188

4.5  PQM Remote Monitoring and Configuration Software	189

Chapter 13	190

Civil Works, Including Buildings and	190

Related Installations	190

1.  General Description of the Project	191

2.  Scope of Supply and Services	193

2.1  General	193

2.2  The Civil Works in the Substations	194

2.3  Instructions Related to the Scope of Works	194

2.4  Design and Engineering	195

2.5  Site-Related Surveys	196

2.6  Soil Investigations	197

2.7  Site Development Works	197

2.8  Site Installation and Temporary Works	198

3.0  Main Civil Works	202

3.1  General Layout	202

3.2  Control Building	203

Internal Finish Schedule — Flooring, Walls, Ceiling, Doors and Windows	206

3.3  Gatehouse	208

3.4  Warehouse Building	209

3.5  Outdoor Foundations	210

3.6  Roads, Paving and Surfacing	212

3.7  Boundary Wall	216

3.8  Chain Link Fences and Gates	219

3.9  Stormwater Drainage System	221

3.10  Sanitary Sewage Drainage	221

3.11  Landscaping	221

3.12  Retaining Wall Construction	222

3.13  RCC-Framed Gatehouse with Steel Truss Roof	222

3.14  RCC Framed Pump House	222

3.15  RCC Framed Overhead Water Tank	222

4.0  General Design Requirements	223

4.1  Instructions for the Basic Design	223

4.2  Particular Architectural Requirements	224

4.3  Responsibilities of the Contractor	224

4.4  Codes and Standards	227

4.5  Design Loads	227

4.6  Foundation Design	229

4.6 Foundation Types	229

4.7 Design Criteria	230

4.8 Special Civil Design Requirements	231

4.9 Cable Trenches (General)	233

5. Requirements for the Execution of Civil Works	234

5.1 General Stipulations	234

5.2 Site Facilities for the Employer's Representative	234

5.3 Communication System	235

5.4 Responsibilities of the Contractor	235

5.5 Site Services during Construction	236

5.6 Earthworks and Excavation	237

Fill Materials	238

5.7 Site Finishing	239

Switchyard Surfacing	240

5.8 Shallow Foundations	240

5.9 Concrete Works	241

Striking Period for Cast-in-Situ Concrete	245

5.10 Formwork	246

5.11 Drainage	247

Type A — Bedding on Existing Soil	248

Type B — Bedding on a Layer of Sand or Gravel	248

Type C — Concrete Support	248

Type D — Concrete Enclosure	248

5.12 Cable Trenching	250

5.13 Structural Steel	251

Structure Types	251

5.14 Grouting Works	253

5.15 Finishing Works	253

5.16 Stone and Brick Masonry	254

5.17 Non-Structural Steelwork	255

5.18 Wall Covering	256

5.19 Rendering	256

5.20 Corrosion Protection of Steel and Ironwork Generally	256

5.21 Raised Modular Floors	257

5.22 Floor Coverings	257

5.23 Roofs	257

5.24 Doors and Windows	258

5.25 Glazing	258

5.26 Painting (Except Steel Surfaces)	258

6. Geotechnical Investigations	259

6.1 General	259

6.2 Scope of Works for Geotechnical Investigations	259

6.3 Field Work	260

6.4 Laboratory Tests (not limited to)	261

6.5 Results of Geotechnical Investigations	262

6.6 Reporting	263

7. Water Supply System	264

8. Sanitary Wares	265

8.1 Sanitary Sewage Drainage	266

9. Stormwater Drainage System	266

10. HVAC and Heating System Works	267

11. Fire Detection and Protection System	267

11.1 Fire Risk Assessment	268

11.2 Fire Detection	268

11.3 Automatic Fire Detection Systems	268

11.4 Manual Call Points	269

11.5 Alarm and Warning Systems	269

11.6 Fire Alarm Control Panel	269

11.7 Layout Display Board	270

11.8 Detection System Elements	270

11.9 Ionization Detectors	270

11.10 Optical Smoke Detector (Photoelectric)	271

11.11 Flame Detector (UV Type)	272

11.12 Manually Operated Push Buttons (MCP)	273

11.13 Sirens (Audible Alarms)	273

12. Structural Protection	274

12.1 Material	274

12.2 Fire Barriers and Fire Compartments	274

12.3 Walls and Ceilings	274

12.4 Roofs	275

12.5 Cable Ducts, Cable Trenches	275

13. Portable Fire Extinguishers	275

Applicable Standards	275

13.1 Types of Fire Extinguishers	275

13.2 Construction and Materials	276

13.3 Performance Requirements	276

13.4 Mounting and Installation	276

13.5 Inspection, Testing, and Maintenance	276

13.6 Documentation	276

14. Technical Specification for Water Well Construction	276

14.1 Scope	276

14.2 Selection of a Well Site	277

Minimum Distances from Pollution Sources	278

14.3 Applicable Standards	278

14.4 Site Investigation	278

14.5 Drilling Method	278

14.6 Casing and Screen	278

14.7 Well Development	279

14.8 Pump Installation	279

14.9 Well Head Completion	279

14.10 Test for Quality of Water	279

14.11 Test for Sand	279

14.12 Test for Yield and Drawdown	280

Time Intervals for Drawdown and Recovery Readings	280

14.13 Disinfection	280

Appendix - I: Technical Data Sheets	281

A. Technical Characteristics of System	281

B. Required and Guaranteed Technical Requirements and Characteristics of Equipment — 220 kV Switchyard Equipment	284

220 kV Circuit Breaker	284

220 kV Isolators with Earthing Switch	286

220 kV Bus Bar Isolator Switch	288

220 kV Current Transformers	289

220 kV Capacitive Voltage Transformers	291

220 kV Surge Arresters	293

220 kV Post Insulator	294

Equipment Connections — 220 kV Switchyard	295

Overhead Conductors	296

Overhead Ground Wire	296

Insulator String at 220 kV	297

220 kV Bus Bar	298

Steel Structures, Bolts and Nuts	299

C. Power Transformers, Auxiliary Transformers and Diesel Generator	300

220/20 kV Power Transformers	300

Auxiliary Transformers	304

Diesel Generator	306

D. 20 kV Switchyard Equipment (MV Equipment)	308

20 kV Switchgear for Auxiliary Supply and Distribution	308

E. MV, LV Power Cables, Control Cables and Cable Trays	312

MV Power Cables	312

LV Power Cables (0.4 kV) — Single, Three & Four Core	313

0.4 kV Control Cables	314

DC Cables	315

Lighting Cables and Heat-Resistant Cables	315

Cable Trays	316

F. AC/DC Installations	317

0.4 kV Switchgear	317

DC Distribution Panels	318

Battery Chargers (220V DC and 48V DC)	319

Batteries (220V DC and 48V DC)	320

G. Lighting and Small Power Installations	321

H. Earthing and Lightning Protection Systems	322

I. Protection and Control	323

# Chapter 01

# Scope of Supply of Plant and Services

## 1. General Information:

The Qush Tepa and Darzaab Substation Project is part of the Electrification of Qush Tepa and Darzaab Districts Project, initiated by the Ministry of Energy and Water (MEW) of the Islamic Emirate of Afghanistan (IEA) to provide a reliable and sustainable electricity supply to these districts through connection to the National Power Grid.

Qush Tepa and Darzaab Districts are located in Jawzjan Province and are currently not connected to the National Electric Power Network. The development of new substations in these districts is a key component of the electrification program, enabling the integration of the local distribution networks with the national transmission system and ensuring a stable power supply for residential, commercial, agricultural, and public sector consumers.

This specification covers the engineering, design review, procurement, manufacturing, transportation, installation, testing, and commissioning of the proposed Qush Tepa 220/20 kV Substation and Darzaab 220/20 kV Substation. The scope of works includes all civil, structural, electrical, and auxiliary systems required for the complete and reliable operation of the substations.

The major works under this specification include, but are not limited to, the construction of substation buildings and civil facilities, installation of 220 kV and 20 kV switchgear systems, power transformers, protection and control systems, SCADA and communication systems, auxiliary power supply systems, battery and charger systems, grounding and lightning protection systems, metering systems, fire protection systems, and all associated equipment and facilities required for safe operation.

The Contractor shall be responsible for the complete execution of the substation works, including detailed engineering (where applicable), procurement, manufacturing, factory acceptance testing, transportation, installation, site testing, commissioning, preparation of as-built drawings, operation and maintenance manuals, and training of the Employer’s personnel.

All works shall comply with the requirements of the Ministry of Energy and Water, the approved project documents, applicable international standards, and relevant technical specifications. The substations shall be designed and constructed to provide a reliable, safe, and efficient power supply system with adequate provisions for future expansion.

The project shall be implemented within the period specified in the Contract Documents. Upon successful completion and commissioning, the Qush Tepa and Darzaab Substations shall provide the necessary interface between the high-voltage transmission system and local distribution networks, supporting the long-term electrification and development of both districts.

Figure 1: Qushtepa substation

Figure 2: Darzaab Substation

1.1. Project Location:

| Substations | Latitude | Longitude |
| --- | --- | --- |
| Qushtepa SS | 36.253344° | 65.466069° |
|  | 36.253811° | 65.465108° |
|  | 36.252969° | 65.464572° |
|  | 36.252547° | 65.465553° |
| Darzaab SS | 35.992439° | 65.371042° |
|  | 35.991789° | 65.371717° |
|  | 35.992747° | 65.373622° |
|  | 35.993453° | 65.372953° |

### 1.2 Climate and Geographic Condition:

- Altitude:

Qushtepa SS: Approx. 630 meters

Darzaab SS: Approx. 1100 meters

- Dry Priod:

Qushtepa SS: June to November

Darzaab SS: June to November

- Rainy Priod:

Qushtepa SS: December to May

Darzaab SS: December to May

- Annual Rain Fall:

Qushtepa SS: 200 mm

Darzaab SS: 200 mm

- Air Temperature:

Qushtepa SS: Max (15 °C), 	Average (45 °C), 		Min (-10 °C)

Darzaab SS:	 Max (15 °C), 	Average (45 °C), 		Min (-10 °C)

- Air Humidity:

Qushtepa SS: Max (60 %), 	Min (15 %)

Darzaab SS:   Max (60 %), 	Min (15 %)

- Thermal Resistivity of Soil:

Qushtepa SS: Max (3.0 °C m/w), 	Average (1.2 °C m/w)

Darzaab SS: 	 Max (3.0 °C m/w), 	Average (1.2 °C m/w)

- Maximum Solar Radiation:

Qushtepa SS: 1200 W/m

Darzaab SS: 	1200 W/m

- Maximum Wind Velocity:

Qushtepa SS: 41 m/sec

Darzaab SS:   41 m/sec

- Wind and Dust:

Qushtepa SS: Sand and Dust Storms in Summer

Darzaab SS: 	Sand and Dust Storms in Summer

## 2. SCOPE OF SUPPLY AND SERVICES FOR 220/20 kV QUSHTEPA AND DARZAAB SUBSTATIONS

### 2.1 General Requirements

The Contractor shall be responsible for the complete detailed engineering, design, procurement, manufacture, assembly, factory testing, inspection, supply, transportation, delivery, unloading, storage, installation, erection, testing, commissioning, energization, trial operation, training, documentation, and handover of the Qushtepa and Darzaab 220/20 kV Substations.

The Works shall be executed on a complete turnkey basis. The Contractor shall provide all equipment, materials, systems, structures, facilities, accessories, services, and works necessary to deliver two fully operational, safe, reliable, efficient, maintainable, and integrated 220/20 kV substations.

The scope of supply and services shall include all 220 kV outdoor switchyard equipment, 220 kV transmission-line bays, transformer bays, busbar systems, bus-section or bus-coupler facilities where required, 20 kV metal-clad switchgear, transformer incomer panels, outgoing feeder panels, bus-section and bus-coupler panels, 220/20 kV power transformers, transformer cooling systems, transformer monitoring systems, protection and control systems, substation automation systems, SCADA and RTU systems, telecommunications and tele-protection systems, AC and DC auxiliary power systems, station-service transformers, battery banks, battery chargers, DC distribution systems, UPS systems, power cables, control cables, protection cables, communication cables, fiber-optic systems, cable trenches, cable ducts, cable trays, cable-support systems, earthing systems, lightning-protection systems, indoor and outdoor lighting systems, civil works, structural works, architectural works, mechanical works, control buildings, relay rooms, battery rooms, communication rooms, equipment foundations, gantries, support structures, transformer foundations, transformer rail systems, transformer oil-containment and drainage systems, internal roads, access roads, drainage systems, fire-detection and fire-protection systems, CCTV systems, security systems, access-control systems, testing and commissioning, training, spare parts, special tools, technical documentation, operation and maintenance manuals, and final as-built documentation.

The Contractor shall provide all equipment and materials complete in every respect. All fittings, supports, clamps, connectors, terminals, cable glands, cable lugs, internal wiring, external wiring, auxiliary relays, communication interfaces, software, software licenses, engineering tools, test equipment, special tools, spare parts, and accessories required for the safe and reliable operation of the substations shall be included in the scope of supply.

Any equipment, material, component, service, work, or facility that is not specifically identified in the Contract documents but is necessary for the completeness, proper operation, safety, reliability, maintainability, or satisfactory performance of the substations shall be deemed to be included in the Contractor’s scope without additional cost to the Employer.

All equipment and materials shall be new, unused, of proven design, and suitable for continuous operation under the environmental and electrical conditions applicable to the Project. The equipment shall be suitable for the specified ambient temperature, altitude, humidity, solar radiation, wind, dust, pollution level, seismic conditions, system voltage, system frequency, loading conditions, and short-circuit levels.

The Contractor shall coordinate all electrical, protection, control, SCADA, telecommunication, civil, structural, mechanical, and operational interfaces with the existing and future electrical networks. The interface scope shall include the incoming 220 kV transmission lines, remote-end substations, 220 kV transmission-line bays, existing electrical networks, future electrical networks, incoming and outgoing 20 kV feeders, distribution networks, protection systems, control systems, SCADA systems, substation automation systems, telecommunication systems, tele-protection systems, and national, regional, or local control centers.

The Contractor shall perform all required interface studies and coordination studies and shall ensure complete compatibility between the Qushtepa and Darzaab Substations and the connected electrical networks.

The Contractor shall provide all required provisions for future expansion, including adequate equipment space, foundations, support structures, busbar extensions, cable trenches, cable ducts, cable routes, control-panel space, protection-system capacity, SCADA-system capacity, communication-system capacity, and auxiliary-system capacity, as required by the approved design and the Employer.

The Contractor shall inspect the project sites and shall familiarize itself with the site conditions, topographical conditions, geological conditions, climatic conditions, access conditions, existing facilities, utility interfaces, transportation conditions, and all other conditions that may affect the execution of the Works. The Contractor shall be fully responsible for considering all such conditions in its design, construction planning, supply, installation, testing, and commissioning activities.

All engineering studies, calculations, analyses, designs, drawings, technical submittals, equipment selections, manufacturing documents, construction documents, testing procedures, and commissioning procedures shall be submitted to the Employer for review and approval. Approval by the Employer shall not relieve the Contractor of responsibility for the correctness, completeness, safety, reliability, performance, or compliance of the Works.

The Contractor shall comply with the Contract requirements, applicable Afghan laws and regulations, applicable IEC and IEEE standards, internationally recognized standards, and good engineering practice. Any design, equipment, material, installation, or construction work found not to comply with the Contract requirements shall be corrected, modified, repaired, or replaced by the Contractor without additional cost to the Employer.

### 2.2 Detailed Engineering and Design

The Contractor shall prepare all detailed engineering documents required for the procurement, manufacture, construction, installation, testing, commissioning, operation, maintenance, and future expansion of the Qushtepa and Darzaab 220/20 kV Substations.

The Contractor shall perform all engineering studies, calculations, analyses, simulations, designs, and technical evaluations required to demonstrate that the substations will operate safely, reliably, efficiently, and satisfactorily under normal operating conditions, abnormal operating conditions, emergency conditions, and applicable short-circuit conditions.

The detailed engineering shall include the preparation of design criteria, design-basis documents, technical specifications, equipment data sheets, electrical single-line diagrams, electrical three-line diagrams where required, general arrangement drawings, site-layout drawings, equipment-layout drawings, electrical connection drawings, control schematics, protection schematics, wiring diagrams, interconnection diagrams, cable schedules, cable-routing drawings, cable-trench drawings, earthing drawings, lightning-protection drawings, civil drawings, structural drawings, architectural drawings, mechanical drawings, foundation drawings, construction drawings, SCADA-system architecture drawings, communication-system drawings, testing and commissioning procedures, operation and maintenance manuals, and final as-built drawings.

All engineering documents shall be prepared by qualified and experienced engineers and shall be checked and approved in accordance with the Contractor’s quality-management procedures before submission to the Employer.

#### 2.2.1 Electrical Engineering

The Contractor shall perform all electrical engineering studies, calculations, analyses, and designs required for the complete and coordinated design of the substations.

The electrical engineering shall include the preparation of electrical single-line diagrams, electrical three-line diagrams where required, load-flow studies, power-flow studies, maximum and minimum short-circuit calculations, fault-level studies, equipment-duty calculations, protection-coordination studies, protection-selectivity studies, protection-setting calculations, earthing-system calculations, soil-resistivity studies, step-voltage calculations, touch-voltage calculations, insulation-coordination studies, lightning-protection calculations, switching-surge studies where required, transformer sizing calculations, transformer impedance calculations, transformer vector-group verification, transformer cooling calculations, auxiliary AC-load calculations, auxiliary DC-load calculations, station-service transformer sizing calculations, battery sizing calculations, battery-duty-cycle calculations, battery-charger sizing calculations, UPS sizing calculations, cable sizing calculations, cable ampacity calculations, cable derating calculations, cable short-circuit withstand calculations, voltage-drop calculations, busbar sizing calculations, busbar thermal-withstand calculations, busbar electrodynamic-withstand calculations, loss calculations, reliability studies, availability studies, power-quality studies where required, harmonic studies where required, SCADA-system engineering, telecommunication-system engineering, substation automation-system design, control and protection-panel design, metering-system design, lighting-system design, emergency-lighting calculations, and all other studies required for the complete design of the substations.

The electrical design shall consider the maximum system voltage, nominal system voltage, system frequency, maximum and minimum fault levels, thermal short-circuit withstand capability, peak short-circuit withstand capability, equipment interrupting capability, insulation levels, switching overvoltages, lightning overvoltages, future expansion requirements, reliability requirements, availability requirements, operational flexibility, maintainability, personnel safety, equipment safety, environmental conditions, seismic requirements, compatibility with existing electrical networks, compatibility with remote-end substations, and compatibility with the existing protection, SCADA, and communication systems.

The Contractor shall verify all electrical-system parameters with the Employer and the relevant system operator before finalizing the detailed design.

#### 2.2.2 Civil and Structural Engineering

The Contractor shall perform all civil, structural, architectural, geotechnical, drainage, road, and associated engineering required for the complete construction and operation of the Qushtepa and Darzaab 220/20 kV Substations.

The Contractor shall conduct all necessary topographical surveys, geotechnical investigations, soil investigations, soil-bearing-capacity assessments, material investigations, and site assessments required for the detailed design.

The civil and structural engineering shall include site-development plans, site-grading plans, earthwork calculations, cut-and-fill calculations, excavation designs, backfilling designs, foundation designs, foundation calculations, reinforced-concrete designs, structural-steel designs, equipment support-structure designs, gantry-structure designs, busbar-support-structure designs, transformer foundation designs, transformer rail-system designs, transformer oil-collection-pit designs, transformer oil-containment-system designs, transformer oil-drainage-system designs, cable-trench designs, cable-duct designs, cable-pit designs, drainage-system designs, stormwater-management designs, internal-road designs, access-road designs, control-building designs, relay-room designs, control-room designs, battery-room designs, communication-room designs, boundary-wall designs, perimeter-fence designs, guard-house designs, fire-protection civil works, architectural finishes, waterproofing designs, thermal-insulation designs, building-ventilation arrangements, and all other civil and structural works required for the complete Project.

All foundations and structures shall be designed for the applicable dead loads, live loads, equipment loads, wind loads, seismic loads, thermal loads, short-circuit forces, operating loads, maintenance loads, transportation loads, installation loads, and all other applicable design loads.

The structural design shall comply with the latest applicable editions of ACI 318, ASCE 7, applicable ASTM standards, applicable IEC standards, applicable ISO standards, applicable Afghan construction requirements, applicable seismic-design requirements, and other internationally recognized standards approved by the Employer.

The Contractor shall submit complete structural calculations, design assumptions, load combinations, material specifications, reinforcement details, connection details, and construction drawings for review and approval by the Employer.

### 2.3 220 kV Outdoor Switchyard

The Contractor shall design, manufacture, supply, transport, install, test, commission, energize, and hand over complete 220 kV outdoor switchyards for the Qushtepa and Darzaab Substations.

The 220 kV switchyards shall include all transmission-line bays, transformer bays, busbar systems, bus-section or bus-coupler facilities where required, metering facilities, future expansion provisions, circuit breakers, disconnect switches, earthing switches, current transformers, capacitive voltage transformers, surge arresters, busbar conductors, busbar support structures, gantries, steel structures, post insulators, insulator strings, clamps, connectors, flexible conductors, rigid conductors, busbar droppers, control systems, protection systems, local control facilities, SCADA interfaces, communication interfaces, cables, foundations, earthing connections, lightning-protection facilities, and all accessories required for complete and satisfactory operation.

The 220 kV switchyard configuration shall be in accordance with the approved single-line diagram and final detailed design.

The Contractor shall provide all required provisions for future expansion, including equipment space, foundations, support structures, busbar extensions, cable routes, cable trenches, cable ducts, control-system capacity, protection-system capacity, communication-system capacity, and SCADA-system capacity.

#### 2.3.1 220 kV Transmission-Line Bays

Each 220 kV transmission-line bay shall be complete with a 220 kV SF₆ circuit breaker, motor-operated disconnect switches, motor-operated earthing switches, current transformers with sufficient protection and metering cores, capacitive voltage transformers, surge arresters with surge counters and leakage-current monitoring, main and backup line-protection systems, bay-control units, local control facilities, protection and control panels, tele-protection equipment, communication interfaces, SCADA interfaces, event-recording facilities, disturbance-recording facilities, control cables, protection cables, auxiliary cables, fiber-optic cables, line-termination equipment, gantry connections, insulator strings, conductor clamps, OPGW connection facilities where applicable, and all required fittings and accessories.

The line-protection systems shall be coordinated with the protection systems at the remote-end substations. The Contractor shall perform all necessary protection-coordination studies, communication-interface studies, and end-to-end protection tests.

#### 2.3.2 220 kV Transformer Bays

Each 220 kV transformer bay shall be complete with a 220 kV SF₆ circuit breaker, motor-operated disconnect switches, motor-operated earthing switches, current transformers with sufficient protection and metering cores, capacitive voltage transformers where required, surge arresters with surge counters and leakage-current monitoring, transformer protection systems, bay-control units, local control facilities, protection and control panels, SCADA interfaces, control cables, protection cables, auxiliary cables, fiber-optic cables, transformer connections, and all required fittings and accessories.

#### 2.3.3 220 kV Busbar System

The Contractor shall provide complete 220 kV busbar systems in accordance with the approved single-line diagram and final detailed design.

The busbar system shall include all main busbars, bus sections, bus couplers where required, busbar conductors, busbar support structures, post insulators, busbar clamps, connectors, expansion joints, busbar droppers, flexible connections, rigid connections, busbar earthing arrangements, busbar protection systems, busbar metering facilities, and future busbar extensions.

The bus-coupler bay, where required, shall be complete with a 220 kV SF₆ circuit breaker, motor-operated disconnect switches, earthing switches, current transformers, voltage transformers where required, protection and control systems, bay-control units, local control facilities, SCADA interfaces, control cables, protection cables, auxiliary cables, and all required fittings and accessories.

### 2.4 20 kV Metal-Clad Switchgear

The Contractor shall design, manufacture, supply, transport, install, test, commission, energize, and hand over complete 20 kV metal-clad switchgear for the Qushtepa and Darzaab Substations.

The 20 kV switchgear shall include transformer incomer panels, outgoing feeder panels, bus-section panels, bus-coupler panels, metering panels, voltage-transformer panels, station-service transformer feeder panels, busbar systems, vacuum circuit breakers, current transformers, voltage transformers, earthing switches, protection relays, control equipment, metering equipment, local control facilities, SCADA interfaces, communication interfaces, internal arc protection, arc-detection systems where required, mechanical interlocking systems, electrical interlocking systems, busbar protection systems where required, power cables, cable terminations, cable glands, cable lugs, surge arresters, control cables, auxiliary cables, and all required accessories.

The number and arrangement of the switchgear panels shall be in accordance with the approved single-line diagram and final detailed design.

The switchgear shall be designed to permit safe operation, inspection, maintenance, testing, isolation, and future expansion.

The Contractor shall provide adequate space and provisions for future switchgear expansion, including spare panel locations, busbar extensions, cable routes, control-system capacity, protection-system capacity, communication-system capacity, and SCADA-system capacity.

### 2.5 220/20 kV Power Transformer System

The Contractor shall design, manufacture, supply, transport, deliver, unload, install, erect, test, commission, energize, and hand over complete 220/20 kV power-transformer systems for the Qushtepa and Darzaab Substations.

The power transformers shall be three-phase, oil-immersed transformers suitable for continuous operation under the specified electrical and environmental conditions.

The transformer rating, voltage ratio, impedance, vector group, tap range, cooling arrangement, insulation level, short-circuit withstand capability, and other technical characteristics shall be as specified in the approved technical data sheets and final detailed design.

Each transformer shall be complete with a main tank, magnetic core, high-voltage windings, 20 kV windings, insulation system, transformer oil, first complete oil filling, high-voltage bushings, 20 kV bushings, neutral bushings where required, on-load tap changer, tap-changer drive mechanism, tap-changer control system, conservator tank, Buchholz relay, pressure-relief device, oil-level indicator, oil-temperature indicator, winding-temperature indicator, radiators, cooling fans, cooling control system, marshalling box, transformer control cabinet, silica-gel breather, drain valves, sampling valves, oil-filter valves, filling valves, transformer monitoring system, transformer protection system, remote tap-changer control cubicle, automatic voltage-regulation system, transformer rail system where required, and all necessary accessories.

The transformer system shall comply with the latest applicable editions of IEC 60076, IEC 60296, IEC 60354, IEC 60567, IEC 60551, IEC 60214, IEC 61850, applicable IEEE standards, applicable Afghan requirements, and other internationally recognized standards approved by the Employer.

The transformers shall be designed to withstand all applicable thermal, dielectric, mechanical, electrodynamic, transport, installation, seismic, and short-circuit stresses.

### 2.6 Transformer Protection and Control

The transformer protection system shall be designed in accordance with the approved protection philosophy and shall provide reliable, selective, fast, coordinated, and secure protection.

The transformer protection philosophy shall include independent main and backup protection systems. Where applicable, the main and backup protection systems shall use separate numerical protection relays, separate current-transformer cores, independent DC supplies, independent trip circuits, and separate circuit-breaker trip coils.

The transformer protection system shall provide transformer differential protection, restricted earth-fault protection, phase overcurrent protection, earth-fault protection, sensitive earth-fault protection, directional overcurrent protection where required, directional earth-fault protection where required, negative-sequence protection, thermal-overload protection, overfluxing protection, overvoltage protection, undervoltage protection, breaker-failure protection, trip-circuit supervision, lockout protection, Buchholz protection, oil-temperature protection, winding-temperature protection, low-oil-level protection, sudden-pressure protection, pressure-relief protection, tap-changer protection, cooling-system failure protection, transformer-monitoring alarms, event recording, disturbance recording, and fault recording.

All protection relays shall be numerical, multifunctional, and compatible with IEC 61850. The protection systems shall be fully integrated with the transformer circuit-breaker control system, transformer cooling system, on-load tap-changer control system, automatic voltage-regulation system, substation automation system, SCADA system, local control system, remote control center, alarm system, event-recording system, and disturbance-recording system.

The Contractor shall calculate all protection settings and shall submit the protection studies and proposed settings to the Employer for review and approval before commissioning.

The Contractor shall perform complete protection testing, including relay-configuration verification, protection-setting verification, secondary-injection testing, primary-injection testing where required, functional testing, interlocking testing, trip-circuit testing, end-to-end testing, SCADA signal testing, remote-control testing, alarm testing, event-recording verification, disturbance-recording verification, and commissioning tests.

### 2.7 Control and Protection Systems

The Contractor shall provide complete control and protection systems for all 220 kV and 20 kV equipment.

The control and protection systems shall include numerical protection relays, control relays, bay-control units, local control panels, mimic diagrams, circuit-breaker control switches, disconnect-switch control switches, earthing-switch control switches, local and remote control selectors, automatic and manual control selectors, synchronizing facilities where required, multifunction meters, annunciator systems, alarm systems, event recorders, disturbance recorders, fault recorders, interface relays, test switches, terminal blocks, auxiliary relays, control cables, protection cables, fiber-optic interfaces, communication interfaces, IEC 61850 interfaces, SCADA interfaces, and all required auxiliary equipment.

All control and protection systems shall be fully integrated with the substation automation and SCADA systems. The systems shall be capable of receiving control commands and transmitting analog values, digital values, equipment status, alarm information, event information, disturbance information, protection information, and metering information to the local and remote control centers.

The Contractor shall provide adequate space and provisions for future expansion of the control, protection, SCADA, communication, and auxiliary systems.

### 2.8 220 kV Busbar Protection System

The Contractor shall provide complete low-impedance busbar protection systems for the 220 kV busbars.

The busbar protection system shall provide high-speed and selective fault clearance and shall include independent measurement of each phase, complete busbar-zone selectivity, automatic testing facilities, current-transformer ratio compensation, future expansion capability, busbar differential protection, breaker-failure protection, overcurrent supervision, event recording, disturbance recording, fault recording, alarm functions, and communication interfaces.

The busbar protection system shall be fully coordinated with the 220 kV circuit breakers, bay-control systems, substation automation system, and SCADA system.

### 2.9 220 kV Transmission-Line Protection and Control

Each 220 kV transmission line shall be provided with complete main and backup protection systems.

The line-protection systems shall be coordinated with the protection systems installed at the remote-end substations. The Contractor shall perform all required protection-coordination studies, tele-protection studies, communication studies, interface studies, and end-to-end protection tests.

The line-protection system shall provide distance protection, line differential protection where required, directional earth-fault protection, tele-protection, phase overcurrent protection, earth-fault protection, negative-sequence protection, overvoltage protection, undervoltage protection, auto-reclosing protection, synchronism-check protection, breaker-failure protection, thermal-overload protection, trip-circuit supervision, event recording, disturbance recording, and fault-location functions.

The main and backup protection systems shall, where applicable, use separate numerical protection relays, separate current-transformer cores, independent DC supplies, independent trip circuits, and separate circuit-breaker trip coils.

The communication system for line protection and tele-protection shall be provided through OPGW, fiber-optic communication systems, or other communication systems approved by the Employer.

### 2.10 20 kV Protection and Control

The Contractor shall provide complete protection and control systems for all 20 kV transformer incomers, outgoing feeders, bus sections, bus couplers, station-service transformer feeders, metering feeders, and cable feeders.

The protection systems shall provide phase overcurrent protection, earth-fault protection, directional overcurrent protection where required, directional earth-fault protection where required, differential protection where required, thermal-overload protection, undervoltage protection, overvoltage protection, negative-sequence protection, arc-flash protection, breaker-failure protection, trip-circuit supervision, event recording, disturbance recording, fault recording, alarm functions, and communication interfaces.

All 20 kV protection relays shall be numerical, multifunctional, and compatible with IEC 61850.

### 2.11 Substation Automation System, SCADA, and RTU

The Contractor shall provide complete substation automation, SCADA, RTU, control, monitoring, communication, and data-acquisition systems for both substations.

The systems shall provide local monitoring, local control, remote monitoring, remote control, data acquisition, alarm management, event recording, disturbance recording, sequence-of-events recording, historical data storage, equipment-status monitoring, analog measurement monitoring, energy metering, protection monitoring, transformer monitoring, on-load tap-changer monitoring and control, and complete integration with the applicable control centers.

The Contractor shall provide all required RTUs, station controllers, bay-control units, SCADA servers, operator workstations, engineering workstations, communication gateways, network switches, network routers, firewalls, time-synchronization systems, GPS clocks where required, network-management systems, communication cables, fiber-optic cables, software, software licenses, configuration tools, engineering tools, and accessories.

The substation automation and SCADA systems shall support IEC 61850, IEC 60870-5-101, IEC 60870-5-104, DNP3, and other communication protocols required by the Employer or the relevant system operator.

### 2.12 AC Auxiliary Power System

The Contractor shall provide complete AC auxiliary power systems for both substations.

The AC auxiliary power systems shall include station-service transformers, main AC distribution boards, AC sub-distribution boards, automatic transfer systems, auxiliary generators where required, AC power cables, auxiliary sockets, lighting supplies, heating supplies, ventilation supplies, air-conditioning supplies, fire-system supplies, security-system supplies, control and monitoring facilities, protection devices, alarms, and all required accessories.

The AC auxiliary system shall be designed to provide reliable and continuous power to all normal and essential substation loads.

### 2.13 DC Battery and Charger System

The Contractor shall provide complete DC auxiliary power systems including battery banks, battery chargers, DC distribution boards, DC feeder panels, battery-monitoring systems, battery-test facilities, DC cables, DC protection devices, DC alarms, communication interfaces, SCADA interfaces, and all required accessories.

The battery systems shall be designed in accordance with the approved duty cycle and shall provide sufficient capacity to supply all protection, control, communication, SCADA, emergency-lighting, circuit-breaker operating, and essential auxiliary loads during the specified loss-of-AC-supply period.

The battery chargers shall provide automatic operation, battery charging, battery maintenance, load supply, alarm functions, monitoring functions, and communication interfaces.

### 2.14 UPS System

The Contractor shall provide complete UPS systems for all essential substation loads.

The UPS systems shall include UPS units, battery banks, battery chargers, static bypass systems, maintenance bypass systems, UPS distribution panels, monitoring systems, alarm systems, communication interfaces, SCADA interfaces, cables, protection devices, and all required accessories.

The UPS systems shall provide uninterrupted and regulated power to the designated essential loads during normal operation and loss of the main AC auxiliary supply.

### 2.15 Cable Systems

The Contractor shall provide complete cable systems for both substations.

The cable systems shall include 20 kV power cables, low-voltage power cables, control cables, protection cables, instrumentation cables, communication cables, fiber-optic cables, cable trays, cable ladders, cable trenches, cable ducts, cable conduits, cable pits, cable supports, cable cleats, cable glands, cable lugs, cable terminations, cable joints, cable identification systems, cable fire barriers, cable fire stopping, cable sealing systems, earthing connections, and all required accessories.

All cables shall be selected and installed in accordance with the approved cable-sizing calculations, voltage-drop calculations, short-circuit calculations, cable-derating calculations, environmental conditions, installation conditions, and applicable standards.

### 2.16 Earthing and Lightning-Protection Systems

The Contractor shall provide complete earthing and lightning-protection systems for all 220 kV switchyards, 20 kV switchgear, power transformers, control buildings, auxiliary buildings, equipment structures, gantries, fences, cable systems, communication systems, and all metallic structures.

The Contractor shall perform soil-resistivity measurements and shall design the earthing systems in accordance with IEEE 80, applicable IEC standards, and the approved engineering design.

The Contractor shall calculate and verify the earthing-conductor size, earthing-grid configuration, earthing-conductor quantity, conductor burial depth, step voltage, touch voltage, ground-potential rise, surface treatment, equipment earthing, structure earthing, fence earthing, and all other applicable parameters.

The lightning-protection systems shall comply with applicable IEC standards, NFPA 780 where applicable, and other standards approved by the Employer.

### 2.17 Indoor and Outdoor Lighting

The Contractor shall provide complete indoor and outdoor lighting systems for the 220 kV switchyards, transformer areas, 20 kV switchgear rooms, control buildings, control rooms, relay rooms, battery rooms, communication rooms, internal roads, access roads, substation entrances, maintenance areas, guard houses, emergency exits, and all other required areas.

The lighting systems shall include normal lighting, emergency lighting, security lighting, maintenance lighting, external floodlighting, lighting-control panels, lighting circuits, lighting cables, lighting supports, lighting fixtures, emergency-lighting supplies, and all required accessories.

The lighting systems shall provide adequate illumination for normal operation, maintenance, emergency operation, safety, security, and night-time activities.

### 2.18 Fire Detection and Fire Protection

The Contractor shall provide complete fire-detection, fire-alarm, and fire-protection systems for both substations.

The systems shall protect the power transformers, control buildings, control rooms, relay rooms, battery rooms, communication rooms, cable basements, cable trenches, switchgear rooms, auxiliary rooms, and all other areas required by the approved fire-protection design.

The fire-protection systems shall include fire-detection panels, smoke detectors, heat detectors, flame detectors, fire-alarm devices, manual call points, audible alarms, visual alarms, fire-suppression systems, transformer fire-protection systems, fire extinguishers, fire barriers, fire walls, fire-rated cable systems, fire stopping, communication interfaces, SCADA interfaces, and all required accessories.

The fire-detection and fire-protection systems shall comply with the applicable standards and approved fire-protection design.

### 2.19 CCTV, Security, and Access-Control Systems

The Contractor shall provide complete IP-based CCTV, security, and access-control systems for both substations.

The CCTV systems shall provide complete surveillance of the 220 kV switchyards, transformer areas, 20 kV switchgear areas, substation entrances, access gates, guard houses, control buildings, control rooms, relay rooms, and other areas required by the approved security design.

The systems shall include fixed cameras, pan-tilt-zoom cameras where required, cameras suitable for outdoor operation, cameras suitable for low-light operation, CCTV servers, network video recorders, storage systems, RAID backup systems, CCTV workstations, high-resolution monitors, CCTV control equipment, communication networks, remote-access facilities, SCADA interfaces, control-center interfaces, software, software licenses, and all required accessories.

The Contractor shall coordinate the CCTV-camera locations with the outdoor and security-lighting systems to ensure effective surveillance during both daytime and nighttime operation.

### 2.20 Testing, Commissioning, Energization, and Trial Operation

The Contractor shall perform all factory acceptance tests, routine tests, type tests, special tests, site acceptance tests, pre-commissioning tests, commissioning tests, functional tests, protection tests, control tests, interlocking tests, SCADA tests, communication tests, tele-protection tests, end-to-end tests, primary-injection tests, secondary-injection tests, transformer tests, switchgear tests, circuit-breaker tests, disconnect-switch tests, instrument-transformer tests, earthing tests, cable tests, battery tests, battery-charger tests, UPS tests, lighting tests, fire-system tests, CCTV tests, remote-control tests, energization tests, and trial-operation tests required for the complete acceptance of the substations.

The Contractor shall submit complete testing and commissioning procedures, test programs, test schedules, test acceptance criteria, and test reports for review and approval before commencing the testing and commissioning activities.

The Contractor shall correct all defects, failures, nonconformities, malfunctions, and unsatisfactory test results before energization and final acceptance.

### 2.21 Training

The Contractor shall provide complete theoretical and practical training for the Employer’s operation, maintenance, engineering, protection, control, SCADA, communication, and technical personnel.

The training shall include substation operation, safe working procedures, transformer operation, transformer maintenance, circuit-breaker operation, circuit-breaker maintenance, disconnect-switch operation, instrument-transformer maintenance, protection-system operation, protection-relay configuration, protection-relay settings, protection testing, SCADA operation, substation automation operation, communication-system operation, battery-system maintenance, UPS maintenance, fire-system operation, CCTV-system operation, fault diagnosis, troubleshooting, preventive maintenance, corrective maintenance, emergency operation, and all other activities required for the safe and reliable operation and maintenance of the substations.

The Contractor shall provide complete training manuals, training presentations, operating procedures, maintenance procedures, practical demonstrations, and training records.

### 2.22 Employer Participation in Factory Acceptance Tests

The Employer and the Employer’s Representative shall have the right to inspect and witness factory acceptance tests for all major equipment and systems.

The Contractor shall provide adequate advance notice of each factory acceptance test and shall submit the factory test procedures, test programs, test schedules, test equipment details, test acceptance criteria, and relevant technical documents for review and approval.

The Contractor shall provide all necessary support, access, facilities, test information, technical assistance, and documentation required for Employer participation in the factory acceptance tests.

### 2.23 Testing and Measuring Facilities

The Contractor shall provide all materials, instruments, measuring devices, test equipment, test facilities, temporary facilities, personnel, and technical support required for factory testing, site testing, pre-commissioning, commissioning, energization, trial operation, and final acceptance.

All test instruments and measuring devices shall be suitable for the required tests and shall have valid calibration certificates.

### 2.24 Transportation, Delivery, Handling, and Storage

The Contractor shall be responsible for all transportation, customs clearance, delivery, unloading, handling, lifting, movement, storage, preservation, and protection of all equipment and materials.

The Contractor shall provide all required transportation equipment, lifting equipment, handling equipment, unloading equipment, cranes, lifting accessories, temporary storage facilities, preservation materials, and site transportation facilities.

The Contractor shall ensure that all equipment and materials are properly protected against damage, moisture, dust, corrosion, vibration, impact, and deterioration during transportation, unloading, handling, storage, and installation.

### 2.25 Mandatory Spare Parts and Special Tools

The Contractor shall provide all mandatory spare parts required for installation, testing, commissioning, initial operation, preventive maintenance, corrective maintenance, repair, and replacement.

The spare-parts supply shall include all required transformer spare parts, circuit-breaker spare parts, disconnect-switch spare parts, switchgear spare parts, protection-relay spare parts, control-system spare parts, SCADA-system spare parts, communication-system spare parts, battery-system spare parts, UPS spare parts, CCTV-system spare parts, fire-protection-system spare parts, cable accessories, fuses, lamps, relays, auxiliary components, and other items required for the reliable operation and maintenance of the substations.

The Contractor shall provide all special tools, test tools, maintenance tools, lifting tools, handling tools, software tools, configuration tools, engineering tools, and diagnostic tools required for the operation and maintenance of the supplied equipment and systems.

### 2.26 Documentation

The Contractor shall provide complete technical, engineering, manufacturing, construction, testing, commissioning, operation, maintenance, training, and as-built documentation.

The documentation shall include all design documents, engineering calculations, engineering studies, technical specifications, equipment data sheets, approved drawings, construction drawings, installation drawings, general arrangement drawings, wiring diagrams, control schematics, protection schematics, cable schedules, cable-routing drawings, earthing drawings, lightning-protection drawings, SCADA documents, communication documents, protection settings, protection-coordination studies, factory test reports, site test reports, commissioning reports, energization reports, trial-operation reports, operation manuals, maintenance manuals, training manuals, spare-parts lists, special-tools lists, software documentation, software licenses, configuration files, engineering files, final as-built drawings, and final as-built documents.

All final documents shall accurately reflect the equipment and systems supplied and the final configuration installed at the Qushtepa and Darzaab Substations.

### 2.27 Limits of Supply and Interfaces

The Contractor’s scope shall include complete Qushtepa and Darzaab 220/20 kV Substations, including all 220 kV switchyard bays, 220 kV busbar systems, 220 kV transmission-line interfaces, 220 kV transformer bays, 220/20 kV power transformers, 20 kV switchgear, 20 kV incoming and outgoing feeders, protection systems, control systems, substation automation systems, SCADA and RTU systems, communication and tele-protection systems, AC and DC auxiliary systems, battery and UPS systems, cable systems, earthing systems, lightning-protection systems, lighting systems, civil works, structural works, architectural works, mechanical works, fire-protection systems, CCTV systems, security systems, testing and commissioning, energization, trial operation, training, documentation, mandatory spare parts, special tools, and all other equipment, materials, works, and services required for the complete and satisfactory operation of the substations.

The Qushtepa and Darzaab 220/20 kV Substations shall be delivered complete in every respect and shall be fully tested, commissioned, energized, safe, reliable, operational, maintainable, and ready for satisfactory continuous service.

# Chapter 02

# General Project Requirements and Documentation

Tabel of Content

## 1. General

All information, documentation, calculations, drawings and schedules relating to the Qush Tepa 220/20 kV Substation and the Darzaab 220/20 kV Substation shall be submitted within the periods and at the dates necessary to guarantee smooth handling of the Project without delay. The Contractor is responsible for submitting all documentation in accordance with the program specified in the Contract, allowing the Ministry of Energy and Water (MEW), acting as Employer, and the Project Manager sufficient time to check, assess, comment on and approve the documents. The quality of the submitted documents must be in accordance with acceptable international practice so as to allow an expeditious checking procedure. Documents that do not fulfil these requirements will be returned to the Contractor without comment, for improvement and resubmission.

The following types of documents are generally to be considered under this Contract:

- Correspondence (letters, faxes and e-mails);

- Drawings and diagrams (design, manufacturing, detail, preliminary, construction and as-built);

- Approval files for major and key equipment, design calculation sheets and technical data sheets;

- Factory test records;

- Site test records;

- Testing programs;

- Training programs;

- Reports and minutes of meetings; and

- Operation and maintenance instructions and manuals.

It is of the utmost importance that all documents relating to the Qush Tepa and Darzaab Substations are exchanged between the Contractor, the Employer (MEW) and the Project Manager in an organized manner, in strict accordance with these procedures and the Contract Documents.

All documentation in electronic format shall use standardized software compatible with Microsoft Office. Upon request, all documents shall be handed over by the Contractor in electronic form, in the electronic format in which the document was originally prepared.

## 2. Bidding Stage

The drawings issued with the Bidding Documents for the Qush Tepa and Darzaab Substations are intended to be descriptive of the character of the works and are to be used in conjunction with the requirements of the Specification. They shall in no way limit the responsibility of the Contractor to supply all plant, equipment, materials and services necessary to provide a complete and functional substation complex, connecting each substation to the National Power Grid. Any omission from the drawings and/or the Specification, or any express reference to a detail or item of work that is nevertheless clearly necessary and intended, shall not relieve the Contractor of the responsibility to include such detail or work within its scope of supply.

Where measurements are affected by conditions already established on site (including the site conditions in Qush Tepa and Darzaab Districts, Jawzjan Province), the Contractor shall take and be responsible for field measurements, notwithstanding any information shown on the Specification drawings.

The Specification drawings portray the basic layout of the scope of works, and the Bidder shall incorporate these requirements into its Bid drawings.

With regard to the interconnections with, and extensions to, existing installations (including the point of connection to the National Power Grid), the drawings and descriptions included in this Specification shall be assumed to be descriptive only, to the extent necessary for bidding purposes.

The Bidder shall submit, together with its Bid, drawings, diagrams, graphs, curves and such other information as is necessary to allow the Bid to be understood from a technical, financial and administrative point of view.

## 3. Contracting Stage

The preparation and compilation of the Contract documents for the Qush Tepa 220/20 kV Substation and the Darzaab 220/20 kV Substation shall be performed by the Contractor under the direction of the Project Manager.

The number of copies of documents required to be submitted by the Contractor is specified in the relevant sub-clauses below.

The cost of reproducing the Contract documents shall be deemed to be included in the Contract price.

### 3.1 Detailed Design and Manufacturing Stage

### General

The Contractor shall prepare and submit for approval all drawings, documents, calculation sheets, diagrams, graphs, curves and other information necessary to verify that the plant, equipment and materials that it intends to manufacture and supply for the Qush Tepa and Darzaab Substations comply in every respect with the requirements of the Contract.

All documents submitted for approval shall be in computerized format. The Contractor shall submit design, construction, installation, operation and maintenance documentation for the entire substations in good time to permit each substation, as a whole, to be erected and commissioned in compliance with the guaranteed timetable.

Such documents and information shall be submitted within the specified time scale, calculated in weeks after the Award of Contract. Further details shall be agreed in accordance with the approval procedure for drawings and documents described in this Section.

### 3.2 Identification on Drawings

The Contractor shall use the plant/equipment identification schedule and the numbering system of the Employer (MEW/DABS) for all drawings and documents relating to the Qush Tepa and Darzaab Substations.

The Contractor shall distribute, within the time set out in this Section, documents for approval to the Project Manager/Employer, in the number of copies laid down in the Contract or as the Employer or Project Manager may reasonably require.

Each design package shall include the relevant texts, calculations, technical data and drawings. All technical and other documentation, other than the General Project or Conceptual Design and the Preliminary Design, shall be submitted to the Employer/Project Manager for approval, forming an integral part of the design.

After Contract signing, the Contractor shall prepare technical documents for the manufacture of equipment and submit them to the Project Manager/Employer for approval. Any manufacturing work carried out prior to such approval shall be at the Contractor's own risk and expense. Factory Acceptance Testing shall be performed on the basis of these documents and the approved testing programs.

After Contract signing, the Contractor shall also prepare the technical documents on the basis of which the installation and civil engineering works for the Qush Tepa and Darzaab sites will be executed (main design and detailed project design) and submit them to the Project Manager/Employer for approval. Installation and civil works shall not commence until such approval has been received.

Based on these documents and the approved testing programs, site acceptance testing, technical inspection, trial operation and preliminary taking-over shall be performed.

The documents to be submitted for approval shall be provided sufficiently in advance of the guaranteed timetable so that any corrections or amendments requested by the Project Manager/Employer, and any resubmission of documents, do not result in delays. The Project Manager/Employer reserves the right to request additional documents from the Contractor as may reasonably be required for a proper understanding of the design and engineering of the plant.

The drawings and documents to be prepared and submitted for approval during this stage are listed in this Section and elsewhere in the Contract, and comprise the following, without limitation.

### 3.3 Requirements

- Reports and documents as stated in the relevant paragraphs of this Section;

- List of proposed sub-contractors/sub-suppliers, and of any replacement thereof, if applicable;

- Outline drawings;

- Drawings of equipment showing overall dimensions, minimum required clearances to neighboring equipment, weights, anchoring and connection details, and required erection working space;

- Layout drawings: general assembly drawings, drawn to true scale, demonstrating that all parts conform to the provisions and intent of the Contract Documents and to the requirements of installation, operation and maintenance, with components identified by a legend;

- Equipment approval files for major plant components (e.g., 220 kV and 20 kV switchgear, power transformers, protection and control panels), verifying compliance of the equipment, prior to procurement and/or manufacture, with the key data of the equipment offered and contracted;

- Cable lists documenting cabling from the terminals of equipment A to equipment B, indicating at least the cable number, description of function, starting and ending point of each wire, cable type, cable length, wire section and number of available spare wires;

- Calculations and design criteria: in addition to the drawings, or wherever the Contract Documents require, the Contractor shall submit appropriate calculations determining the main design criteria, clearly indicating the principles on which they are based. Conceptual design studies shall accompany the Contractor's solution wherever this facilitates understanding;

- Detailed design system documents for the installation/erection of OPGW and underground optical cable, and fiber-optic equipment drawings and route plans;

- Detailed system documents for the installation/erection of 220 kV cable, where required;

- Proposed inspection and testing programs;

- Testing documents/reports of results of all tests on equipment not otherwise foreseen to be tested;

- Training program;

- Operating and maintenance manuals, with a description of all equipment and facilities and detailed operating and maintenance instructions;

- As-built documents (as-built design), including drawings of all equipment; and

- Spare part lists.

### 3.4 Time Schedules, Work Programs

- A detailed time schedule for the design, manufacture, supply, assembly and commissioning of the Qush Tepa and Darzaab Substations, broken down for the principal plant components and all construction works, stating dates for completion of any preparatory work by others that may be necessary. The schedules shall be prepared in Microsoft Project.

- A detailed erection, installation and commissioning schedule, including all information necessary to permit satisfactory erection, assembly and commissioning of the equipment. Detailed instructions for erection shall be submitted together with reduced-size copies of the applicable drawings showing the erection sequence, including information on handling and slinging of major equipment, erection tolerances and special precautions to be taken during installation, testing and commissioning.

- A detailed program for commissioning of each substation.

### 3.5 Electrical Engineering

Documentation submitted under this clause must form an integral part of the designs, instructions, programs and testing reports referred to elsewhere in this Section.

- Electrical single-line diagrams for both the Qush Tepa and Darzaab Substations;

- List of consumers;

- Cable lists, including cable cross-section drawings;

- Standard circuit diagrams for all types of electrical consumers;

- Circuit diagrams for all individual electrical equipment;

- Lists of equipment and devices;

- Lightning protection plans, with details of measuring locations and reports of measurements taken following commissioning;

- EMC concept, including coordinated overvoltage protection;

- Arrangement drawings;

- Power and lighting installation plans;

- General arrangement drawings of required cable trays and cable-laying plans;

- Dimensioned drawings and erection drawings for transformers, switchgear, etc., including frontal and plan views;

- Dimensioned drawings of switching cubicles, including equipment configurations;

- Calculation of mechanical stresses on switchgear due to arcing faults;

- Short-circuit calculations and determination of protection relay settings for protection and auxiliary electrical supplies;

- Protection setting calculations;

- Protection and metering diagrams;

- Insulator strings and conductor fittings;

- Static calculations of all gantries; and

- Drawings of switchyard gantries.

### 3.6 Control and Protection System Engineering

Documentation submitted under this clause must form an integral part of the designs, instructions, programs and testing reports referred to elsewhere in this Section.

- Control system architecture showing all components;

- Layout drawings of the central control room, showing the spatial distribution of desks and panels;

- Layout of electronic/relay rooms, showing spatial distribution of cubicles and racks;

- Detailed dimensions of desks, panels and cubicles;

- Layout of modules within cubicles;

- Description of all functional group controls;

- Engineering drawings;

- Internal connection diagrams, external connection diagrams, terminal connection diagrams, combined schematic and circuit diagrams, and instrument loop diagrams;

- Instrument hook-up drawings;

- List of recorders/selector switches;

- Instrument list;

- List of annunciations;

- List of alarms, trips and status indications;

- Protection relay setting calculations; and

- Protection relay constellation drawings.

### 3.7 Erection Stage

This clause governs the documentation to be prepared, submitted and maintained during the erection stage at the Qush Tepa and Darzaab Substation sites, as further described in Clauses 3.8 to 3.11 below.

### 3.8 Documentation for Final Erection Checks

Documentation for final erection checks shall comprise check sheets covering all components and sections of the works.

Each check sheet shall contain, as a minimum, the following information:

- Designation of the substation (Qush Tepa or Darzaab);

- Designation of the part of the plant or works subject to the check;

- Reference to the "as-built" documents for the relevant part of the plant or works;

- A table of all checks to be performed for the relevant part of the plant or works;

- Results of the checks and any deficiencies identified; and

- Date of rectification of any deficiencies.

The Project Manager shall approve this documentation prior to the commencement of the Final Erection Checks.

### 3.9 As-Built Drawings and Documents

Documents recording the works as completed ("as-built" documents) shall be prepared by the Contractor and forwarded to the Employer/Project Manager for approval.

All as-built documentation shall represent the latest condition of the plant and shall include all changes, corrections and modifications made after commissioning and energization. Following approval, the documents shall be returned to the Contractor for distribution, in the required number of copies, to the Employer/Project Manager. The documentation shall be in sufficient detail to enable the Employer to maintain, dismantle, reassemble and adjust all parts of the works.

The as-built records and drawings shall include drawings of all equipment and cabling as finally installed and approved by the Project Manager, together with diagrams, graphs, plans, lists and manuals, including a detailed table of contents and all necessary information on replacement parts and operating instructions. These documents shall also be provided in electronic format as agreed with the Employer/Project Manager.

The Contractor shall accept and incorporate the Employer's numbering system into the as-built documents, if requested, without extra cost.

As a minimum, the as-built documentation shall include:

- Single-line drawings;

- Protection diagrams;

- Earthing plan;

- Outline drawings;

- Layout drawings;

- Wiring and connection diagrams and calculations;

- Technical data sheets;

- Cable lists;

- Line/route profile drawings for associated interconnections;

- Insulator strings and conductors' fittings;

- Static calculations of all steel structures and foundations;

- Drawings of all foundations;

- Any other relevant drawing requested by the Employer/Project Manager; and

- All documents updated with modifications made on site, up to acceptance of the works.

For any future extensions to, or modifications of, the Qush Tepa or Darzaab Substations, the as-built documents shall also include the original existing electrical equipment and existing building parts affected by the extension or modification.

In addition to hard copies, the Contractor shall submit each as-built documentation package as an AutoCAD or AutoCAD-compatible file. The "as-built" documents shall be set up in an orderly manner (in files, with a table of contents on the front and inside cover, and a register) and shall be subject to the Employer's/Project Manager's approval. All final records and drawings shall be in the English language.

### 3.10 Commissioning Documentation

The commissioning documentation for the Qush Tepa and Darzaab Substations shall comprise, as a minimum:

- A list of tests to be performed during cold and hot commissioning and during energization;

- A sequence describing how the tests shall be performed;

- A description of the tests and arrangement of the test equipment, including the definition of test equipment to be used;

- Form sheets on which the test results are to be recorded during the tests; and

- A list of test equipment, including technical details, to be used.

Approval of the commissioning documentation shall be a prerequisite for the commencement of commissioning tests.

### 3.11 Documentation for Taking Over

The documentation for taking over shall comprise the following documents:

- Certificate for Final Erection Checks, including the deficiency list and any open deficiency items;

- Certificate of commissioning, together with the test results of the commissioning tests;

- Deficiency list arising during the tests;

- Agreed tests and procedures for tests to be conducted after completion;

- Form for the Taking-Over Certificate; and

- Financial status of all works, including Variation Orders.

Approved and complete documentation, as described above, shall be a prerequisite for issuance of the Taking-Over Certificate.

### 3.12 Operation and Maintenance Instructions, Manuals

The Contractor shall furnish to the Employer complete operation and maintenance manuals, together with separate operating instructions, for the Qush Tepa and Darzaab Substations. The price of these documents shall be deemed to be included in the Contract price.

The operation and maintenance manuals shall contain a detailed description of the equipment and components, written so as to enable the Employer's personnel to operate, maintain, dismantle, reassemble and adjust all parts.

The manuals shall conform to a table of contents and be as comprehensive and precise as possible. Every effort shall be made to use material specific to this Contract, and nomenclature and references shall be consistent throughout each manual.

The manuals shall be accurate, easy to understand, and presented so that their contents can be used to instruct the Employer's personnel in the operation, service, maintenance and repair of the substations and their individual components. Tables, lists, graphic presentations and explanatory diagrams shall be used as far as possible for ease of understanding.

Instruction and maintenance manuals shall be supplied in CD or equivalent digital format, together with a complete equipment list and spare parts list, and, where applicable, reader software. An indexed electronic link between the index and contents shall be provided.

The information provided shall be complete for main and auxiliary equipment and systems supplied by the Contractor. Information that does not contribute to an understanding of the design, operation or maintenance of the equipment shall be excluded, where appropriate.

Draft instruction manuals shall be submitted no later than three (3) months before the start of commissioning of the respective substation. One original document shall be submitted first, for review by the Project Manager/Employer; following approval, five (5) copies of the final operation and maintenance manuals shall be provided.

Drawings, diagrams, pictures or photographs shall be used where they add to the understanding and clarity of the text. All material shall be free from stamps commonly used for identification of a customer or order number. Precautions and warnings relative to the safety of personnel and equipment shall be included where required.

The operation and maintenance manuals and instructions shall be supplied in bound folders, as agreed with the Project Manager, and shall contain at least the following information:

- Table of contents, with each volume marked and containing the complete table of contents;

- List of illustrations; and

- Operation instructions.

Documentation for the operation and maintenance of instrumentation and control (I&C) equipment shall be unified in structure, design and cross-references, even where the documents are supplied by different subcontractors.

The maintenance manuals shall contain a complete and accurate description of the plant, its assembly and dismantling, and of all components and accessories, including a list of clearances, fits, tolerances and temperatures, as required.

If it emerges, during erection, commissioning, post-completion testing or the warranty period, that the operation and maintenance instructions or operating instructions are inadequate or faulty, and if such deficiency is only discoverable after commissioning and proper setting of the equipment, the Contractor shall carry out and supply the necessary corrections and supplements, free of charge. Revised drawings shall be resubmitted.

The Operation and Maintenance Manuals shall comprise the following main information:

- General and functional description of the substation system and its components, including system capacities and adjustments;

- Technical data and characteristics of each component, included in the operation manuals of the components;

- Test certificates of equipment and materials, for tests performed in the manufacturer's workshops;

- Final erection documentation;

- Commissioning documentation; and

- Taking-over documentation, including spare parts.

The maintenance manuals shall be divided into sections dealing with different maintenance activities, as follows.

(a) Maintenance instructions.

A maintenance schedule shall set out the inspection and maintenance intervals for each item of equipment or part, together with an exact description of the operations to be carried out and the necessary spare parts and materials. This section shall be divided into two subsections:

- Preventative maintenance, indicating the periodic inspections required, the inspection procedure, routine cleaning and lubrication procedures, routine safety checks, calibration checks and similar matters; and

- A "Trouble-shooting guide" describing, for repair and adjustment, the inspection, removal and replacement of parts; electrical, fluid or mechanical circuit tracing; and repair, adjustment, calibration and commissioning procedures. The Contractor shall set out the intervals for exchange of equipment to be replaced during operation, expressed in number of operating cycles or years of service. Necessary dismantling/erection instructions shall be given in detail.

(b) Spare parts.

The Contractor shall state how and where additional spare parts may be ordered, specifying for each part the ordering number and the name, address, telephone number and e-mail address of the manufacturer or supplier.

### Arrangement

The operating and maintenance instruction manuals shall be suitably bound within a hard cover. All documentation forming part of the manuals shall be of uniform size, except where pull-out or folding charts are provided, and shall use a uniform type and print size. Photographs, exploded diagrams and other pictorial aids shall be used, wherever possible, to assist operating and maintenance procedures.

Cross-section/exploded views shall indicate complete lists of parts, drawing references and gauge settings, together with setting dimensions, tolerances, bolt-tightening torque, calibration, levels and alignment data, lubrication data and history, site repairs, modification history and works/site test results.

All information in the manuals shall be specific to the materials supplied under this Contract; purely typical information shall not be used in its existing, generic form. Information shall always be precise, particularly as regards time intervals, which shall be clearly defined and not expressed as "occasionally" or similar.

### 3.13 Documents Preparation and Submission

The Contractor shall prepare all necessary documents, giving full and complete information, to enable the Employer/Project Manager to properly consider the design of the works.

Documents originated by any Subcontractor shall fulfil all specified requirements and standards. Prior to submittal, the Contractor shall verify measurements, size of members, materials and details, to ensure conformity with the requirements and intent of the Technical Requirements. Documents originated by Subcontractors shall be submitted by the Contractor, and not directly by the Subcontractors.

Documents shall be submitted to the Employer/Project Manager in a sequence such that the information required by the Project Manager for examination purposes corresponds with the progress of the works.

The Contractor shall ensure that all documents for approval are forwarded to the Employer/Project Manager in a manner allowing sufficient time for examination, and that documents are submitted early enough to permit amendments and re-submission for approval without delaying the delivery and installation program or the guaranteed completion dates of the works.

The Contractor shall submit for approval a document list indicating the dates on which documents will be submitted for approval. This list shall be updated periodically (monthly) to indicate the status of document approval, including the document number and the estimated submission date.

All documents prepared or furnished by the Contractor shall be marked with the title of the works, certified by the Contractor and the Subcontractor respectively, and transmitted to the Employer/Project Manager. Each transmittal of documents shall be accompanied by a Document Transmittal Sheet (DTS), indicating the titles and numbers of the documents transmitted.

At monthly intervals, or as otherwise agreed, the Contractor shall submit copies of its complete document lists, incorporating the updated schedule referred to above, together with the latest transmittal sheets. These lists shall clearly indicate the status of every document (for information only, for approval, resubmitted for approval, approved, or as-built).

Modified documents shall bear a revision field and revision date, and the nature of the modification shall be clearly stated, whether or not the document was previously approved, approved on condition, revised or not approved.

All documents shall bear the approved Contract references and title block agreed with the Employer/Project Manager. At least the following information shall be included in the title block:

- The Contractor's name;

- The Subcontractor's name, where applicable;

- The Employer's name (Ministry of Energy and Water);

- The Project name (Electrification of Qush Tepa and Darzaab Districts Project);

- The name of the Project Manager;

- A brief description of the contents of the drawing;

- Drawing and revision number;

- First date and revision dates;

- Scale and scale bar, where applicable; and

- Space for the Employer's drawing number.

All drawings shall be plotted using metric units, and all descriptive wording shall be in the English language. All drawings and other documents shall conform to one of the sizes set out in international standard ISO 216, as follows:

| Size | Dimension of Trimmed Drawing (Finished Sheet) |
| --- | --- |
| A0 | 1,189 mm × 841 mm (maximum) |
| A1 | 841 mm × 594 mm |
| A2 | 594 mm × 420 mm |
| A3 | 420 mm × 297 mm |
| A4 | 297 mm × 210 mm |

All the above formats shall be folded to size A4, with a margin for binding. The following scales shall be used:

- For reductions: 1:2.5; 1:5; 1:10; 1:20; 1:50; 1:100; 1:200; 1:500; 1:1000; 1:2000; 1:2500.

- For enlargements: 2:1; 5:1; 10:1.

In addition to the sizes mentioned above, horizontally extended sizes are permissible, for example for circuit diagrams, wiring diagrams and route plans, which shall have a height of 297 mm and a length that is a multiple of 210 mm.

The quality of original drawings, master prints, blue-prints and all other copies, irrespective of the method of production, must be such that no damage, including partial or complete illegibility, can occur as a result of extreme climatic conditions, having regard to the local conditions in Jawzjan Province. A paper grade weighing no more than 80 g/m² shall be used throughout for drawings. Logical and graphical symbols, as well as abbreviations used in the drawings, shall be identified in a legend, with abbreviations described in full text.

Drawings released for construction must contain all information necessary for the execution of the works. Drawings shall be to scale and fully detailed, with a maximum size of DIN A0 (840 mm × 1,190 mm). Important dimensions shall be given, and the material of which each part is to be constructed shall be indicated. Drawings shall be shown as black lines on a white background, with revisions clearly marked. Drawings under this Contract shall be prepared in the English language.

Documents that have been approved shall not be changed without the written permission of the Employer/Project Manager.

The Contractor shall be responsible for any discrepancies, errors or omissions in the documents and other particulars supplied by it, whether or not such documents and particulars have been approved by the Employer/Project Manager. Where such errors or omissions are discovered later, they shall be made good by the Contractor at its own expense, irrespective of any prior approval.

If, during the Contract period, the Contractor is required to increase the size of any foundations or similar items shown on its Bid drawings, in order to accommodate the finally approved arrangement of the works (with due allowance for access, lay-down and maintenance), such increases shall be deemed to be included within the Scope of the Contract.

The Project Manager and the Employer shall have the right, at all reasonable times, to inspect at the Contractor's factory all documents relating to any portion of the works. If requested, the Contractor shall submit design calculations and shop drawings.

The Contractor shall, within the times specified in the Contract, provide drawings showing the manner in which the plant is to be assembled, together with all information relating to the works and required for preparing suitable foundations, providing suitable access for the plant and any necessary equipment to the erection point on site, and making all necessary connections to the plant, whether or not such connections are to be made by the Contractor under the Contract.

Any expense resulting from an error, omission or delay in the delivery of necessary documents and information shall be borne by the Contractor.

The indicative document submission schedule for the Qush Tepa and Darzaab Substations is set out below, expressed in weeks after the effective date of the Contract. Purpose codes: A = for approval; I = for information only.

| Document | Purpose | Preliminary | Final |
| --- | --- | --- | --- |
| General project information / current list of drawings | I | 4 | Every month |
| Quality assurance program | A | - | 6 |
| Health, safety and environment plan | A | - | 8 |
| Weekly progress report | I | - | Every week |
| Erection and installation progress reports | I | - | Every month |
| List of subcontractors/manufacturers | A | 8 | 12 |
| Type test reports (certificates) with the Bid and documents for approval | A | 8 | 12 |
| Proposed inspection and testing programs, including test procedures | A | 8 | 16 |
| Detailed commissioning program, including commissioning documentation | A | - | 12 weeks ahead of start |
| Report of results of all tests | A | - | 4 weeks after each test / as part of O&M manuals |
| Training program | A | - | 24 |
| O&M manual with description of equipment and facilities | A | - | 3 months ahead of commissioning |
| Detailed operating and maintenance instructions | A | - | 2 months ahead of commissioning |
| As-built documentation, including drawings of all equipment | A | - | 4 weeks before taking-over |
| Spare part lists | I | - | 10 |
| Payment schedule | I | - | Every 4 weeks |

| Document | Purpose | Preliminary | Final |
| --- | --- | --- | --- |
| Overall time schedule (design, manufacture, supply, assembly, commissioning) | A | With Bid | 12 |
| Detailed erection, installation and commissioning schedule | A | 4 | Updated every month |
| Complete list of documents with proposed submission deadlines | I | 4 | 8 |
| Design data | A | 6 | 10 |
| Performance calculations | I | 8 | 10 |
| Design calculations | A | 8 | 16 |
| Structural calculations | A | 8 | 16 |
| Electrical single-line diagrams | A | - | 6 |
| Functional/interlocking diagrams, protection relay calculation and setting diagram | A | 8 | 12 |
| Circuit diagrams for all electrical circuits, including interlocking | I | 12 | 16 |
| Layout drawings, including equipment location | A | With Bid | 16 |
| Arrangement drawings, including dismantling and sectional views | A | 8 | 12 |
| Sectional and detail drawings of all components | I | 8 | 12 |
| Lifting plan for all lifting operations | I | 8 | 12 |
| Steel structure calculations | A | 8 | 12 |
| Workshop drawings for steel structures, including details | A | 12 | 14 |
| Arrangement drawings for MV and HV cables | A | 8 | 12 |
| Drawings of cable routing | A | 8 | 12 |
| Arrangement drawings of control and relay rooms | A | 12 | 12 |
| Communication arrangement and installation drawings | A | 8 | 12 |
| Detailed foundation drawings | A | 10 | 14 |
| Load information | A | 8 | 12 |
| Steel structure assembly drawings | I | 8 | 16 |
| Drawing lists, regularly updated | I | 8 | Updated every four weeks |
| Factory test schedules | A | - | 1 month ahead |

### 3.14 Drawings and Documents Approval Procedure

#### 3.14.1 General

All information and documents relating to the Qush Tepa and Darzaab Substations, including calculations, drawings and schedules, shall be submitted within such periods or at such dates as are required to guarantee smooth handling of the Project without delay. The sequence of submission shall ensure that information is available for the timely approval/review of each document upon receipt. The Contractor is responsible for submitting all documents, allowing all participants sufficient time to check, assess, comment on and approve them. The quality of the submitted documents must be in accordance with acceptable international practice, to allow an expeditious checking procedure. Documents not fulfilling these requirements will be returned to the Contractor without comment, for improvement and resubmission.

The Employer/Project Manager will give approval within four (4) weeks of receipt of documents. Any manufacturing work carried out prior to such approval shall be at the Contractor's own risk and expense. If the Employer/Project Manager fails to approve or comment on documents within this period, the Contractor may proceed with fabrication once that period has elapsed.

The Contractor shall be responsible for any discrepancies, errors, mistakes, omissions or deficiencies in the documents, or in the material and equipment subsequently supplied, whether or not such documents have been approved.

Each document for which no approval is required shall be clearly marked "For information only" on the Documents Transmittal Sheet; the Employer/Project Manager may nonetheless decide to treat such a document as submitted for approval, if deemed necessary. Each document submitted for approval shall be clearly marked "For approval"; the Project Manager may, however, decide to mark such a document "Not subject to approval", if deemed necessary.

The Contractor must not, in any case, distribute a document without one of the above markings, or the mark "Approved…". Documents distributed without such marking may be regarded as non-existent.

The Project Manager reserves the right to require the Contractor to submit additional copies of drawings and other documents for approval to the Project Manager's head office. If the documents conform to the requirements, the Project Manager will return one copy to the Contractor, stamped and approved. If the documents do not fulfil the Contract requirements, the Project Manager will return one copy stamped "Not Approved" to the Contractor, with comments marked thereon, and the drawing shall be amended and resubmitted for approval. The Employer shall receive details of the comments sent to the Contractor.

When submitting drawings for approval, including any drawing prepared by a subcontractor, the Contractor shall certify in each case that it has examined such drawings and that they comply with the requirements of the Contract. For the purposes of this clause, the term "drawing" includes diagrams, schedules and performance curves.

Approval of a drawing by the Project Manager will imply that:

- General arrangement and layout drawings and key diagrams have been examined and appear to be in accordance with the basic design concept of the Contract, and meet the technical requirements of the Specification;

- Other drawings of plant and equipment have been examined in relation to the compatibility of the items and equipment with the Specification, and in respect of interconnections with other items, equipment or systems; and

- Any approval given by the Project Manager shall not relieve the Contractor of its responsibility under the Contract.

The Project Manager will not normally require copies of detailed manufacturing drawings or calculations, but the Contractor shall make these available if so requested.

Drawings are to be submitted and distributed in accordance with the following table:

| Item | Description | Sender | Recipient | Copies |
| --- | --- | --- | --- | --- |
| 1 | For approval | Contractor | Project Manager | Employer |
| 2 | Reviewed | Project Manager | Contractor, with comments | Employer (copy of transmission) |
| 3 | Approved for construction | Contractor | Project Manager | Employer; Project Manager site office |

Any drawing or document serving purely for the purpose of information will not be stamped "Approved", but "Seen by the Project Manager" only.

Upon receipt of approval from the Project Manager, the Contractor shall arrange for the revision column of the drawings to be marked "Approved by the Project Manager on (date)", and shall revise the issue letter or number accordingly.

The Contractor shall ensure that drawings are submitted early enough, prior to the date required for approval, to permit amendments to be made and the drawings re-submitted for approval, without delaying the program of deliveries or the guaranteed completion dates of the works.

If, during the Contract period, the Contractor is required to increase the size of any buildings, foundations, etc., from that shown on its Bid drawings, to accommodate the finally approved arrangement of the works (with due allowance for access, lay-down and maintenance), such increase shall be deemed to be included within the scope of the Contract.

#### 3.14.2 Approval Stages of Drawings

The first drawings to be submitted by the Contractor for the approval of the Project Manager shall be the site layout drawings, single-line diagrams, general arrangement drawings and main equipment drawings for the Qush Tepa and Darzaab Substations. These general drawings shall also address any existing plant and facilities not subject to rehabilitation.

After obtaining approval from the Project Manager, the detailed design of the individual disciplines (mechanical, electrical, civil, etc.) may be completed and submitted for information and/or approval to the Project Manager.

#### 3.14.3 Categories of Approval

As regards documents submitted for approval by the Contractor and reviewed by the Employer and Project Manager, the Contractor will be notified of the results of the review by return of one copy of the document, marked by stamp with one of the following categories:

- "Approved" – AP;

- "Approved with Comments" – AC; and

- "Not Approved" – NA.

The notification "Approved" authorizes the Contractor to commence or proceed with manufacturing or construction, in compliance with its contractual obligations. In this case, the Contractor shall distribute the document, without delay, stamped "FOR CONSTRUCTION". If the document is subsequently modified for any reason, it is understood that the previous notification of the Employer/Project Manager is automatically invalidated; the Contractor is accordingly obliged to notify the Employer/Project Manager immediately of the further modification, to delete the remark "Approved by the Employer/Project Manager on…" from the original document, and to resubmit the document for approval under the same procedure.

The notification "Approved with Comments" authorizes the Contractor to commence or proceed with manufacturing and construction, in compliance with its contractual obligations, subject to all noted corrections having been made and incorporated into the document, and to the Contractor being satisfied that the work and/or equipment at this stage is in full compliance with the Employer's/Project Manager's requirements. Following correction, the document shall be resubmitted for approval within one month of the date of the preceding "Approved with Comments" notification, clearly indicating the reasons for, and details of, the revision.

The notification "Not Approved" indicates that the document must be revised and resubmitted for approval before the Contractor proceeds with manufacture.

The notifications "Approved", "Approved with Comments" and "Not Approved" shall, however, be understood as the result of sample checks only.

During the preliminary stage of its design work, the Contractor may submit documents to the Employer/Project Manager once, for information and general review, to form the basis of eventual design meetings. At the latest, once quality, completeness and conformity with the Contract Documents have reached a satisfactory level, the Contractor shall submit these documents for formal approval; each such document will be reviewed and checked by the Employer/Project Manager to reach the status "Approved", as described above.

Prior to starting any work, the Contractor shall have in hand copies of the pertinent documents that have been approved and issued for construction, and shall supply the required number of copies to the Employer and Project Manager at site, one week prior to the start of the relevant work.

The Employer/Project Manager may order the interruption of the execution of any work for which the Contractor cannot present approved documents at site. Such an interruption shall not relieve the Contractor of its contractual obligations, nor shall it serve as grounds for the Contractor to claim an extension of the construction time.

#### 3.14.4 Submission for Approval

All documents submitted for approval shall be accompanied by a Documents Transmittal Sheet (DTS). The DTS number and submission date shall be indicated on each copy of a document sent for approval. The status (i.e., "Approved", "Not Approved", "Approved with Comments", or "Seen by the Project Manager") shall be stamped by the Employer/Project Manager on the document's covering page.

The DTS shall include the following:

- Document distribution;

- Date of issuance;

- Date of receipt (not mandatory to be completed);

- Emitter's internal references;

- Signature and stamp of the emitter;

- Title of the documents;

- Numbering of the documents in accordance with the agreed procedure, with a clearly identified version number;

- Purpose of the document: for information (FI), for approval (FA) from the Employer/Project Manager, or for a returned document following approval from the Employer/Project Manager (RET);

- Status of approval (to be updated by the Employer/Project Manager, as described under Categories of Approval);

- Date of the Employer's/Project Manager's decision relating to the status;

- Signature and stamp of the authorized Employer/Project Manager representative; and

- Comments and remarks.

Copies of signed DTS forms will be sent to the Contractor.

#### 3.14.5 Documents Distribution

Unless expressly stated otherwise elsewhere in this Contract, the Contractor shall follow the document distribution set out below, for both the Employer's head office (H.O.) and site offices, and for the Project Manager's head office and site offices.

| Document Type | Employer H.O. | Employer Site | Project Manager H.O. | Project Manager Site |
| --- | --- | --- | --- | --- |
| Contract Documents | 3 | - | 1+1* | - |
| Contract Documents (A5) | 3 | - | 1+1* | - |
| Correspondence | 1 | - | 1* | - |
| Documents for approval | 3 | - | 3+1* | 1 |
| Approved drawings | 2* | 1 | 1+1* | 3 |
| As-built design | 3** | 1 | 1+1* | 3 |
| Progress reports | 3 | 3 | 2+1* | 2 |
| Breakdown reports | 3 | 2 | 1+1* | 1 |
| O&M manuals (draft) | 1 | 1 | 1+1* | 1 |
| O&M manuals (final, incl. one soft copy on CD-ROM) | 2 | 4 | 1+1* | 1 |
| Close-out report | 2 | 2 | 1* | 1 |

* Includes one soft copy. ** Includes two soft copies on CD-ROM or equivalent digital medium.

The Contractor shall supply and submit, free of charge, any further copies reasonably required by the Employer/Project Manager.

#### 3.14.6 Photo Documentation

As soon as work commences on the Qush Tepa or Darzaab site, the Contractor shall provide digital color photographs of the works. The Project Manager reserves the right to select the positions from which photographs are to be taken. Up to thirty (30) photographs per month shall be provided in electronic format and in printed form. Each photograph shall bear a description, a serial number and the date on which it was taken.

The Contractor shall also provide, from time to time, as and when required by the Project Manager, further photographs of the works to record or illustrate specific events.

### 3.15 Correspondence

### General

All correspondence addressed to the Employer (MEW) and the Project Manager shall be written in the English language.

All correspondence shall be numbered in accordance with a procedure to be agreed with the Project Manager. Applicable Standard Operating Procedures of the Project Implementation Unit (PIU) shall also be observed when submitting documents to the Employer.

The Contractor's site manager and discipline engineers shall be fluent in spoken and written English.

All correspondence shall be addressed to the Employer, with a copy to the Project Manager, in accordance with the distribution table set out in Clause 3.14.5.

All correspondence shall be prepared, codified and numbered in accordance with the procedure to be described by the Project Manager and the instructions of the Employer.

In addition to the requirements of the Conditions of Contract, all meetings and discussions with the Project Manager shall be conducted in English, and the Contractor shall engage English-speaking supervisors only.

All correspondence shall bear the date of issuance, in the format dd.mm.yyyy. Letters and documents shall be of a quality allowing easy photocopying, and shall be in A4 format.

For classification purposes, correspondence dealing with a mixture of subjects is not permitted. Separate documents shall be prepared for each major technical and commercial topic, to expedite distribution to the relevant discipline engineers.

All correspondence shall be prepared, codified and numbered in accordance with the following structure: Project – Sender – Recipient – Consecutive number.

Through a monthly review of the correspondence logs, it shall be ensured that all correspondence has been received and is followed up properly. For any correspondence, letters or e-mail shall normally be used, and documents/drawings for approval shall be submitted by letter.

E-mail may, in exceptional cases, be used to expedite the procedure by sending documents as attachments; additional information should be avoided within the body of the message. A document sent by e-mail shall be considered valid only after submission of the original letter/document, or upon confirmation by a specific returned message.

A classification system for documents that are not correspondence (i.e., drawings, reports, etc.) shall be applied, the purpose of which is to identify, by a unique number, each document and drawing relating to the Project, providing full information regarding the content of the document and facilitating reference, filing and follow-up. The Contractor shall propose its classification system, fulfilling applicable quality assurance standards (such as ISO 9001), subject to approval by the Employer/Project Manager.

## 4. Project Control and Reporting

The scope of contract control services to be performed by the Contractor shall include, without limitation, functions described under the following major headings:

- Preparation of project controls procedures;

- Project planning and scheduling;

- Project work breakdown structure;

- Project progress measurement;

- Progress certification and invoicing;

- Progress reporting;

- Health, safety and environmental reporting; and

- Environmental Management Plan.

The Contractor shall use computer systems to the maximum extent possible for the project control services listed above. Such systems shall be capable of electronic interface between the Contractor's home offices, the Qush Tepa and Darzaab construction site locations, and the Employer/Project Manager.

The requirements and systems described below are provided for guidance and to establish minimum project requirements. The Contractor may use its own in-house systems, provided that the Employer's/Project Manager's requirements, as stated in the applicable Contract control procedures, are met.

### 4.1 Reporting

#### 4.1.1 Monthly Progress Report

By the fifth working day of each month, the Contractor shall transmit a written Progress Report to the Employer/Project Manager, covering all aspects of the Qush Tepa and Darzaab Substation Project. The report shall include an executive summary describing the global status of the Project, comprising a table of figures and a short narrative covering:

- Percentage of completion against scheduled completion (an S-curve presentation shall be used);

- Financial status, showing actual released payments against scheduled payments;

- Actual values of realized works; and

- Areas of concern and corrective actions.

The main part of the report shall include:

- All activities associated with design, material procurement and manufacture;

- Works tests, shipping, mobilization, site erection, testing and commissioning;

- Procurement progress, delivery details and forecasts, including specific information on late deliveries likely to affect progress;

- The arrival of materials, the progress of manufacture and the date on which equipment will be ready for transport;

- Project execution, detailed by activity, and overall and discipline-wise status of progress, compared with planned progress;

- All special occurrences (such as accidents or defects), which will affect the completion date of the works in the manufacturer's workshops;

- Current and future areas of concern, and status of previously identified areas of concern;

- Remedial actions recommended, correcting or reducing existing or potential problems and delays, and the effectiveness of remedial actions taken for earlier problems;

- Schedule status, highlighting milestone status, status of critical activities, and schedule trend analysis, indicating actions proposed to ensure timely completion of the Contract;

- Number of contractual documents issued by the Contractor and analyzed by the Employer/Project Manager;

- Updated document submittal schedule for the next three months;

- Detailed project Master Plan Schedule prepared in Microsoft Project. After Contract signature, the Contractor shall monthly update the schedule submitted with its Bid, completed with required outages, having regard to the Employer's need to assure safe and continuous operation of the existing grid. The Contractor shall apply for outages two months in advance, and the Employer may negotiate the requested outages in order to meet its obligations towards a satisfactory power supply; the Employer is nonetheless bound to grant outages to the Contractor as set out in the agreed methodology;

- QA/QC matters;

- Prospects for the next two months; and

- Health, safety and environmental matters.

#### 4.1.2 Report Format

The Progress Report shall also include two lists of action items: one list of action items that are currently pending, and another of action items completed during the previous month.

The Progress Report shall also include two correspondence logs for the preceding month: one for transmittals from the Contractor to the Employer/Project Manager, and one for transmittals from the Employer/Project Manager to the Contractor. Each log shall record, for each transmittal (in column format): transmittal number, transmittal date, subject and author.

At least two months in advance, the Contractor shall include additional information in its monthly reports, specifically a list of equipment concerned by the implementation of the test and substation outage programs for equipment shutdown.

#### 4.1.3 Weekly Progress Report

Weekly progress reports shall be prepared and submitted by the Contractor from the start of site construction activities. The weekly progress report shall be submitted to the Employer/Project Manager on the first working day of the following week, and shall, at a minimum, include:

- Brief narratives of the activities performed by each discipline during the week, with highlights of specific achievements;

- Progress tabulation showing planned and actual progress by discipline and in total (S-curves shall be used);

- Areas of concern and proposed corrective action;

- Manpower and construction equipment loading charts;

- Major activities planned for the next week;

- List of outstanding documents and correspondence requiring a response from either the Employer/Project Manager or the Contractor; and

- Sub-contractor status.

#### 4.1.4 Daily Records (Site Diary)

The Contractor shall keep records on site of the daily quantities of work performed, in the form of a site journal. The daily record shall indicate highlights of manpower and major construction equipment employed, material received, key milestones achieved and other major activities of the day. The final form and content of the site journal shall be in accordance with the instructions of the Employer. The site journal shall be made available to the Employer's site representative during site visits and upon request.

#### 4.1.5 Breakdown Reports

From the start of the warranty period until the end of the Contract period, the Contractor shall prepare an incidental special report upon the occurrence of events such as any failure of equipment, extraordinary disturbance, accident, collapse of steel or concrete structures, trips on the operation of switchgear, or any other remarkable incident, indicating in detail the failure and/or incident that occurred, the reason for its occurrence, and the operational consequences for the plant.

The Contractor shall also describe the special activities carried out and the preventive measures taken to allow undisturbed future operation. Each case shall be carefully and thoroughly investigated by the Contractor, to determine the reason for the damage or to reconcile any contradictions. If necessary, additional investigations shall be carried out by the Contractor upon instruction of the Employer/Project Manager.

The relevant report shall, in each case, be prepared with the utmost speed and presented to the Employer/Project Manager for review and approval.

#### 4.1.6 Close-Out Report (Final Report)

The Contractor shall prepare a Final Report on the Contract, to be submitted to the Employer/Project Manager not later than one month after the Taking-Over Certificate for the entire installations has been issued.

The format and content of the Close-Out Report will be communicated to the Contractor at the latest three months before taking-over, but shall, as a minimum, cover:

- Contract definition;

- Contractor's scope of works (contract value);

- Original and final overall contract value, with a detailed explanation for each deviation;

- Original and final schedule, with a detailed, item-by-item explanation for any deviations;

- Problems occurring during project execution and a detailed description of the actions taken;

- Contractor's organization chart(s);

- Taking-Over Certificate, including the deficiency list;

- Performance test calculations and results;

- Test certificates;

- Inspection certificates;

- Acceptance certificates; and

- All final engineering calculations, bound in separate volumes.

This report shall be updated after issue of the Final Acceptance Certificate (FAC), at the end of the warranty period.

### 4.2 Meetings

After the kick-off meeting following the commencement date of the Contract, regular progress review and coordination meetings shall be held between the Employer, the Project Manager and the Contractor; further parties may attend, if needed. The Employer/Project Manager may call further meetings, if demand arises.

Attendance of the Contractor at all meetings is mandatory. Persons representing the Contractor who are authorized to make decisions on Contract matters shall attend all meetings.

In addition to the requirements of the Conditions of Contract, all meetings and discussions with the Project Manager shall be conducted in English, and the Contractor shall engage English-speaking supervisors only.

#### 4.2.1 Monthly Progress Review and Coordination Meetings

Progress review meetings shall be held at weekly and monthly intervals, starting from the commencement date and following the kick-off meeting. The Contractor's progress reports shall be reviewed in detail at these meetings. Dates shall be fixed well in advance in the Project calendar. Monthly management review meetings shall be held at the office of the Project Implementation Unit (PIU) or at the construction site, and shall be attended by the Contractor's senior management personnel.

The main topics for these meetings shall be:

- Progress of works;

- Planned activities for the next period (month);

- Project administrative matters;

- Technical matters; and

- Other matters.

The Contractor shall prepare a monthly presentation of the Contract status to date, prepared on slides or using computerized software for projection.

Minutes of Meeting (MOM) shall be prepared by the Project Manager and presented to the Employer and the Contractor for review and signature. The Contractor shall pay particular attention to the record of actions agreed at all progress review meetings, the dates by which such actions are required to be taken, and the party responsible for carrying them out.

#### 4.2.2 Weekly Commissioning Coordination Meetings

Weekly coordination meetings shall be held at the Project Manager's site office, starting well ahead of commissioning activities. These meetings shall address construction, commissioning and testing progress, the short-term shutdown program, the energizing program, and coordination with related projects within the Electrification of Qush Tepa and Darzaab Districts Project.

## 5. Handing Over of Documents, Goods and Materials

All goods and materials required to be handed over under this Contract, other than the permanent works erected on the Qush Tepa and Darzaab sites, shall be handed over to the Employer by means of handing-over certificates.

The handing-over certificates shall be prepared by the Contractor and signed by the three involved parties, namely the Employer, the Contractor and the Project Manager, for loose delivery of goods and material including, without limitation:

- Construction documents;

- Consumables;

- Chemicals;

- Lubricants;

- Spare parts;

- As-built drawings;

- O&M manuals; and

- Special tools and handling equipment.

The handing-over certificate and the corresponding receipt shall clearly state that all items have been received in a satisfactory condition, as required under the Contract. The Contractor shall be responsible for demonstrating the satisfactory condition of all items delivered to the Employer, including their re-packing for storage on site.

## 6. Computer Hardware and Software

Where computer hardware or software is to be delivered under this Contract, the following clause shall apply.

The version and model of the computer hardware and/or software supplied under this Contract shall be the latest model/version available at the time of commissioning, rather than that quoted in the Bid documents at the time of the Bid. Availability of the version and model, commercially, will be judged based on the manufacturer's press notification.

If the installation/implementation of the hardware and/or software is not successfully completed within the stipulated time schedule, or within six months, whichever is earlier, and if a higher model/version of the hardware and/or software becomes available in the market during that period, the Employer shall have the right/option to instruct the Contractor to supply/upgrade to the latest available model/version of the hardware and/or software.

## 7. Surplus Construction Material

### 7.1 Cable Scrap and Surplus Material

Cable scrap, surplus cables and surplus spare parts accumulated at the Qush Tepa or Darzaab site after completion of the works are the property of the Contractor, within the frame of the lump sum Contract unit prices. They may be taken back or otherwise recycled, at the discretion of the Contractor.

### 7.2 Packing Material

Non-durable, single-use packing material (wooden boxes, wooden shelves, wooden cable drums, etc.) shall be considered included in the lump sum equipment prices and shall, therefore, be handed over to the Employer upon completion of the works.

Durable, multiple-use packing material (transport containers, steel cable drums, steel equipment transport boxes, etc.) shall remain the property of the Contractor and may be taken back or otherwise used, at the Contractor's discretion.

## 8. Health, Safety and Environmental Matters

### 8.1 HSE (Health, Safety and Environment) Management Plan

The Contractor shall, throughout the Contract period (including the Defects Liability Period), establish and implement an HSE management plan in accordance with applicable international guidelines and the laws of Afghanistan.

Environmental and social assessments shall be conducted for the Project. Within these assessments: (i) an Environmental Management Plan (EMP); and (ii) a Land Acquisition and Resettlement Plan (LARP), shall be elaborated, covering, respectively, health, safety and environmental issues, and all aspects of land acquisition, resettlement and compensation for losses affecting the Qush Tepa and Darzaab sites and associated corridors.

The Contractor shall follow these management plans and shall, in addition to its own HSE policy and goals, prepare a project-specific HSE policy, outlining HSE targets and an HSE plan which, following approval by the Employer, shall undergo continuous implementation, updating and improvement throughout the Project phases. The HSE targets shall be achieved through implementation of a Health, Safety and Environmental Management System (HSEMS) during the construction phase.

The Contractor shall designate a person responsible for all HSE issues at the construction site(s). That person shall prepare monthly records of all HSE-relevant incidents, such as workers' accidents (fatal and non-fatal), and shall maintain an employment record giving the name and age of workers employed. This person shall be responsible for maintaining a high health and safety standard at the construction sites, including the wearing of helmets, the provision of ear protection to workers, ensuring that workers are secured while working at height, and regular training of workers in first aid and safe working practices around high voltage equipment. This HSE officer shall also ensure that all subcontractors follow good HSE practice at the construction sites, and shall report monthly to the Employer and to the Project Manager.

Implementation of the HSEMS and follow-up of measures derived from the EMP and LARP shall be regularly monitored by the Social and Environmental Monitoring function within the Project Implementation Unit (PIU), supported by internationally experienced specialists who will supervise the construction sites approximately twice a year and report to the relevant office.

### 8.2 Land Acquisition and Resettlement

Land acquisition and resettlement for the Qush Tepa and Darzaab Substations, and associated works, shall follow the following principles:

- Land acquisition will be avoided or, at least, minimized wherever possible; and

- Compensation for all losses will be fully provided prior to land occupation and the commencement of construction works.

# Chapter 03

# General Technical Requirements

Tabel of Content

## 1. General Technical Requirements

### 1.1 General

The present clauses refer to the general technical requirements for turnkey contracts for the electrical substations covered by this Contract, namely the Qush Tepa 220/20 kV Substation and the Darzaab 220/20 kV Substation (hereinafter referred to individually or collectively as "the Substations").

The following directions, information and technical requirements for design, engineering, layout, manufacturing, erection, installation and testing shall be observed as far as they are applicable for the equipment to be delivered. The requirements stated in this Section of General Technical Requirements are valid for all sections of the technical requirements, except where different, additional and/or special requirements are specified.

The Plant shall be brand new and designed, manufactured and arranged so that it will have a functional design and a pleasant appearance.

### 1.2 Standards and codes of practice

All materials and equipment supplied shall comply in every respect with the latest technical codes of the International Organization for Standardization (ISO). IEC recommendations apply to the electrical equipment.

Goods and special guarantees beyond the scope of ISO and IEC shall conform at least to one of the following standards and codes in the following priority:

- VDE and EN standards

- BS or ASTM

- Other internationally accepted standards, which ensure a quality equal to or higher than the standards mentioned above, but only if these are submitted in the English language edition.

The Contractor must submit a list of standards to be applied for the equipment manufacturing, testing, installation and commissioning, for approval by the Employer/Project Manager.

During the design stage the Contractor shall supply indexed lists (in English) of all standards, codes and their referred associated standards, to which the Plant and Works are to be performed.

The Contractor, subcontractors, sub-suppliers and shops are to be certified according to ISO 9001.

#### 1.2.1 Design, standardization, interchangeability

The equipment shall be designed to facilitate inspection, cleaning, maintenance and repair. The design shall incorporate every reasonable precaution and provision for the safety of all those concerned in the operation and maintenance of the equipment.

The equipment shall be designed to operate satisfactorily under all variations of load and temperature, as may be met in normal usage under the variation in climatic conditions applicable to Jawzjan Province.

Corresponding parts throughout shall be made to gauge and be interchangeable wherever possible.

All equipment performing similar duties shall be of the same type and manufactured in order to limit the stock of spare parts required and maintain uniformity between the Qush Tepa and Darzaab Substations.

### 1.3 Units of measurement

In all correspondence, technical schedules, drawings and instrument scales, the units of the International System of Units (SI) shall be used, including but not limited to: meter, kilogram, second, degree Celsius, Kelvin, ampere, candela, square meter, cubic meter, liter, Newton, bar, Newton per square millimeter, meter per second, revolutions per minute, cubic meter per second, kilogram per second-hour, liter per second, Newton meter, Joule, Joule per Kelvin, Joule per kilogram per Kelvin, Joule per cubic meter, Joule per gram, Watt, Watt per square meter, Watt per meter Kelvin, Newton second per square meter, meter squared per second, Newton per meter, parts per million, microsiemens per meter, Hertz, Coulomb, Volt, Volt per meter, Farad, Ohm, Siemens, Weber, Tesla, Ampere per meter, Henry, Lumen, Lux and Kelvin meter per Watt.

#### 1.3.1 Guaranteed values

The Contractor shall guarantee that the data mentioned on the name plate of the equipment and given in the data sheets will not deteriorate during the life of this equipment under the specified operating and maintenance conditions.

The Contractor shall guarantee the values in the technical data schedule. The Employer reserves the right to reject any equipment that does not respect these values.

#### 1.3.2 Plant and equipment identification

The Contractor shall prepare an "equipment classification system" for each of the two Substations, based on the KKS or AKZ system or similar. IEC-Publication 81346-1 shall apply.

The classification numbers shall appear in all drawings, lists and documents prepared by the Contractor for the project from the initial stage of the contract execution, and shall clearly distinguish between the Qush Tepa Substation and the Darzaab Substation.

The Contractor shall supply all labels, nameplates, instruction and warning plates necessary for the identification and safe operation of the individual equipment and the plant, and all inscriptions shall be in the English language.

All labels, nameplates, instruction and warning plates shall be securely fixed to items of plant and equipment with stainless steel rivets, plated self-tapping screws or other approved means. The use of adhesives will not be permitted.

Nameplates for plant and equipment identification and record purposes shall be manufactured from stainless steel with a mat or satin finish and engraved with black lettering of a size which is legible from the working position.

Warning plates shall be manufactured from stainless steel engraved with white lettering on a red background and sited in the position where they afford maximum safety of personnel.

All equipment within panels and desks shall be individually identified by satin or mat finish stainless steel labels, or laminated plastic labels where approved.

#### 1.3.3 Packing, marking and labeling

The Contractor shall prepare all equipment and materials for shipment in such a manner as to protect them from damage in transit and shall be responsible for and make good any and all damage due to improper preparation or loading for shipment.

Before being packed for shipment to Site, all items of Plant shall be carefully numbered and marked so that they can be readily assembled and erected in the correct relative positions at the respective Site, whether Qush Tepa or Darzaab. Wherever applicable, these numbers and markings shall be punched or painted so that they shall be clearly visible.

Packing shall be done into convenient sections, so that the weight and size of sections are suitable for the transport conditions to Site and for handling at Site under the special conditions applicable there.

All individual pieces shall be marked with the plant identification number and the correct designation shown on the Contractor's detailed drawings and other documents (packing lists, lists in Operating and Maintenance Manuals, etc.), clearly indicating the destination Substation.

All parts of the Plant shall be packed at the place of manufacture. The packing shall be suitable for shipment by sea and/or land and for all special requirements of the transportation to Site.

Where necessary, double packing shall be used in order to prevent damage and corrosion during transportation, unloading, reloading and during intermediate storage.

The individual packages shall have convenient weights and sizes for transport and for handling on Site. All identical members shall be packed together, if reasonably possible, in a form convenient for shipment and handling.

Small items shall be packed in boxes and large items shall be protected, where necessary, by timber, straw and sacking. Drums shall be used for cables and similar materials. All bolts, nuts, washers, etc. shall be packed in containers.

All parts shall be suitably protected against corrosion, water, sand, heat, atmospheric conditions, shocks, impact, vibrations, etc. for transportation and storage.

Spare parts shall be packed for long duration storage. Items such as gaskets and seals shall be vacuum sealed packed.

Each crate or package shall contain a packing list in a waterproof envelope. All items of Material shall be clearly marked for easy identification against the packing list.

All cases, packages, etc. shall be clearly marked on the outside to indicate the total weight, the position of the center of gravity and the correct position of the slings and shall bear an identification mark relating them to the appropriate shipping documents.

All stencil marks on the outside of cases shall be either of a waterproof material or protected by shellac or varnish.

All packing costs shall be included in the scope of delivery. The packing materials shall be disposed of by the Contractor. The costs for the transport and unloading in the storage place, as well as disposal of the packing materials, shall be deemed to be included in the Contract Price.

#### 1.3.4 Transport of material and equipment

Shipment by sea freight shall be made to the designated port of entry, and onward carriage by land to Jawzjan Province shall be made to the Qush Tepa and Darzaab Sites, or as otherwise agreed with the Employer. Airfreight, where used, shall be made to the destination airport agreed with the Employer.

Shipments are to be made in accordance with Incoterms as explained in the commercial conditions.

The Contractor shall ensure that adequate handling equipment is available to unload the heaviest piece of equipment at each Site.

Prior to shipment the Contractor shall furnish by e-mail, fax, or otherwise, as agreed, the shipping documents to the Employer.

When actual transport has been completed, the Employer shall be so notified.

All cases and boxes shall be clearly and boldly marked and shall be sent to the Employer as per address details indicated in the project manual or otherwise agreed with the Employer.

In order to facilitate customs examination, all packages and transport documents shall, regardless of other markings, be clearly and indelibly marked.

#### 1.3.5 Transport Assessment

The Contractor shall prepare and submit to the Employer/Project Manager a transport assessment report for the delivery of equipment to each of the Qush Tepa and Darzaab Sites.

The Contractor's transport assessment report shall include but not be limited to:

- The intended transport route from the point of import into Afghanistan to each Site;

- List of all the regulatory authorities and Land Owners the Contractor has consulted with, details of discussions reached and any approvals/permits issued;

- Transporter drawing (plans/elevation) including general arrangements and sweep paths;

- The method of transport to the final location including transport and pilot vehicles required;

- List of any actions necessary along the transport routes such as remedial actions, strengthening, temporary routes, road closure;

- Proposed transport plan, giving times of transport, all overnight storage locations, security requirements, etc.;

- Where a transportation beam set is being used, the additional transportation requirements should also be included;

- Location and source of wheel sets and traction machinery;

- No historical authority approval or adequacy of clearances for transportation shall be assumed.

#### 1.3.6 Traffic Management

The Contractor shall submit transport and traffic management plans for review by the Employer/Project Manager.

#### 1.3.7 Permits and Approvals

The Contractor shall be responsible for all permits, fees and supervision requirements for land transport.

#### 1.3.8 Heavy lifts

The Contractor shall be responsible for providing all heavy lifting facilities to unload/load heavy equipment at both the Qush Tepa and Darzaab Sites.

### 1.4 Health, Safety and Environmental

#### 1.4.1 Health and Safety

A Safety Manual shall be submitted by the Contractor to the Employer for approval before commencement of site work. All such safety requirements shall conform with the latest applicable health and safety regulations. The Health, Safety & Environmental procedures (HSE-Manual) shall comply with prudent industry practice.

The works and all plant, equipment and materials forming part of this Contract shall comply in all respects with any relevant local Statutory Regulations, By-Laws and Orders currently in force in Afghanistan.

The Contractor shall provide documentation proving such evidence. The Employer shall have the right of refusal of the equipment not so approved.

The Contractor shall provide a full-time Safety Officer at each Site. Maximum safety precautions consistent with good erection practice in all site works must be afforded to personnel directly engaged on this Contract.

Particular care and additional safe-working precautions shall be taken during erection works in the vicinity of live lines and/or at places where there are parallel power lines which may be energized.

Supervision at site by a competent and experienced supervisor is a requirement.

The operation of or connections to any items of equipment once made live shall be subjected to Safety Regulations which require work permits to be issued by an Authorized Person before any work can be carried out.

The Contractor shall provide an alcohol and drugs policy statement.

The Project Manager shall have the right to audit safety procedures and documentation at any stage of the contract. If the Project Manager considers that any operation is in breach of safety legislation, or that the safety of any personnel is compromised by any operation, the Project Manager shall have the right to halt the work.

### 1.5 Environmental Protection Plan

The Contractor shall submit for the approval of the Employer/Project Manager an Environmental Protection Plan (EPP) giving a full account of potential environmental impacts at the Qush Tepa and Darzaab Sites and the mitigation measures which he proposes to employ. This Plan shall demonstrate that environmental concerns are addressed, and adequate measures would be taken to comply with the recommendations made.

The Contractor shall be responsible for the correct implementation of the mitigation measures detailed in the approved version of this EPP Report.

The Environmental Assessment Management Plan shall be strictly followed.

### 1.6 Signs

#### 1.6.1 General

Safety colors, safety symbols and safety signs shall comply in construction, geometrical form, color and meaning with ISO 3864-1: 2011.

Signs of plant identification during the erection period shall be to the Project Manager's/Employer's approval.

The signs should be of a material which is weather resistant and has sufficient durability under the conditions prevailing on site.

The position for the signs must be chosen so that they are within the field of vision of the persons to whom they apply. The signs should be permanently attached. Temporarily dangerous areas (e.g. construction sites, assembly areas) may also be marked by portable signs. The safety signs must be mounted or installed in such a manner that there is no possibility of misunderstanding.

#### 1.6.2 Warning signs

Warning signs shall refer to the existence or possible existence of danger, such as: inflammable or explosive substances, corrosive or noxious substances, suspended loads, general danger, width/height restriction, danger of trapping, steps, slipping, falling, etc. Appropriate black and yellow strip markings should also be used where necessary.

#### 1.6.3 Prohibition signs

Prohibition signs are, for example: no smoking; no fires; no naked lights; no entry to pedestrians; no entry; do not switch on; etc.

#### 1.6.4 Protections, guards, sunshades

Moving machine parts in the open are to be provided with a suitable protection in order to prevent danger to the personnel. These protection devices have to be in accordance with applicable safety regulations.

#### 1.6.5 Hazardous areas

The Contractor shall take full account of any special requirements concerning the nature, handling and storage of fuel oils, gases etc. and make provisions to ensure the safety of the personnel.

#### 1.6.6 Maintenance isolation

All major equipment shall be arranged to facilitate safe isolation from all hazards for maintenance purposes.

### 1.7 Quality Assurance

The Contractor shall have a certified quality assurance system based on the ISO 9000 and ISO 14001 series for the activities in the scope of the company.

The Contractor shall establish a Quality Assurance System under the scope of works included in the Contract.

For this purpose, the Contractor shall prepare and submit a Quality Plan in accordance with the guidelines provided in the draft of ISO 10013, and during the Contract Period in accordance with the latest revision of ISO 10013.

The Quality Plan shall cover all operational procedures which are all activities, services and Works of the Contractor during the Contract Period which shall include but not be limited to the following:

- Design and development, procurement of raw materials

- Manufacturing, testing

- Construction/installation on site

- Commissioning

- Servicing/maintenance

It is understood that all testing and inspections as specified in this document are part of the Quality Plan.

All work shall be witnessed by the Employer/Project Manager who shall have the right to observe any aspect of the work and carry out audits to check compliance with the quality documentation at any stage. The Employer/Project Manager shall have the right to halt the work in the event that significant infringements are identified to the Contract, Technical Requirements, Quality Assurance System, Quality Plan and Operational Procedures.

#### 1.7.1 Quality Plan

After the Commencement Date, the Contractor shall prepare a Quality Plan which shall define the operational procedures and quality control measures for the implementation of the general principles of the Quality Assurance System for the Qush Tepa and Darzaab Substations Project. This Quality Plan shall detail all tests and inspections to be carried out in respect of the following activities but not limited to:

- Type Tests (if applicable)

- Raw materials, components and services inspections

- Manufacturing

- Factory Acceptance Tests

- Site Tests

- Commissioning

The Quality Plan, which shall include the activities of all Sub-Contractors, shall clearly identify the following but not limited to:

- The various significant material supply and installation phases including the Sub-Contractors and their roles.

- A listing of all the quality checks, inspections, and tests to be carried out.

- Documents describing the execution of the above quality checks, inspections and tests together with the relevant acceptance criteria.

- A listing of the various working documents used to record results of such quality checks, inspections, and tests together with sample copies of such documents.

- Non-Conformance Reports "pro forma" together with details of the procedures to be followed in remedying such non-conformances.

- Establishment and Maintenance of Quality Records.

#### 1.7.2 Employer Quality Inspections

The Employer and the Project Manager shall have the right for free access to the Contractor's and any Sub-Contractor's premises during the course of the Contract in order to carry out Quality Inspections which will include, but not be limited to, the following activities:

- Inspection of design documentation, calculations etc.

- Witnessing the Type Tests

- Witnessing the Routine Tests

- Plant visits and inspections during manufacture

- Participation at progress review meetings

- Carrying out Quality Assurance System checks

In order to facilitate such Quality Inspections, the Contractor shall provide the Employer and the Project Manager with a schedule indicating the timing of the principal quality control activities as detailed in the Quality Plan.

#### 1.7.3 Non-Conformances

The Contractor shall provide the Employer and the Project Manager with a Non-Conformance Report for all "major non-conformances" encountered during the Contract. This Report shall contain full details of the non-conformance together with proposals for remedial action. The Employer or Project Manager shall approve such remedial action prior to its implementation by the Contractor.

"Major non-conformances" are considered to be any departures from the requirements set out in the Technical Requirements or in the internal requirements detailed by the Contractor in his Quality Plan.

All other non-conformances, such as departures from internal requirements not specified in the Contractor's Quality Plan, can be considered as minor. Such non-conformances shall also be detailed in a Non-Conformance Report.

#### 1.7.4 Final Quality Report

Following completion of all quality activities carried out during the course of the Contract, the Contractor shall compile a Quality Report. This report shall contain a complete record of the quality activities including, but not limited to, the following:

- The Quality Plan detailing the Quality Assurance System functions and procedures together with the detailed test and inspection program

- The Contractor's Raw Material Specifications

- Certificates of Origin of Raw Materials

- Test and Inspection Reports

- Minutes of Quality Audits

- Non-Conformance Reports

- Resolution of Non-Conformances Reports

### 1.8 Corrosion protection and painting

#### 1.8.1 General

This section is to define surface preparation, protective coatings and paint systems to be applied on equipment and structures unless otherwise specified.

All Plant and Material supplied under this Contract shall be suitably protected by an adequate painting system to withstand any deteriorating impacts caused by the climatic conditions specified for the Qush Tepa and Darzaab area.

Also, standard material and equipment, if provided for this project, requires a painting system which complies with this condition.

The general guides for the work shall be:

- These technical requirements

- DIN EN ISO 12944-1 to 8 or equivalent standards

- Relevant international standards

- The paint manufacturer's product data sheets with related instructions

- The Employer shall have the right for the choice of the color from a color code to be prepared by the Contractor.

#### 1.8.2 Inspection and liability period of corrosion protection and paint

The Contractor and/or paint Contractor shall assist the Project Manager/Employer in making any tests or inspections when, in the opinion of the Project Manager/Employer, such inspection is necessary or required.

Defects which affect the corrosion protection and which are caused either by inadequate workmanship of application or by the coating material must be rectified by the Contractor at his cost.

The Employer reserves the right to decide when these deficiencies shall be rectified.

At commencement of painting up to a stage ensuring permanent high quality of application, and thereafter upon request of the Project Manager/Employer, the paint supplier shall be present at the job site to supervise the application, preparing test patches and covering questions and problems which might arise. All related costs are deemed to be included in the contract price.

No consecutive coats of paint, except in the case of white, shall be of the same shade.

To provide proof of liability, various identified and recorded test patches shall be applied. Should any defect arise during the defects' liability period which is not reflected in the test patches, the reason will be assumed to be inadequate workmanship of application. Should the defect be reproduced similarly in the test patches and the total coated surface, the reason will normally be assumed to be inadequate quality of coating material.

#### 1.8.3 Retained samples

For all coating work, samples must be taken and retained at the job site for possible reference in the event of coating failure. Retained samples must be kept at least until the Contract period has expired.

All paint film thickness quoted in the attached table "Paint Systems" refer to the dry film condition. For final acceptance, a surface area of 10 m² per 100 m² will be taken. Of the 50 single dry-film-thickness measurements, only 5 may be below 10% of the specified dft. If results do not meet specification, additional coats must be applied until the specified thickness is reached. For measuring the dry film thickness, a non-destructive dry film thickness gauge shall be used.

Usually, the required minimum dry film thickness has to be checked for the complete coating system. In specific cases it is necessary to measure the wet film thickness per coat, for example the prime coats.

After coating work is completed, a general final check of the coating application must be made. In certain cases (e.g. tar epoxy linings) commercial high voltage spark testers shall carefully inspect the finished coating system for pinholes in the paint film.

#### 1.8.4 Defects liability related to painting

Defects which affect the corrosion protection, and which are caused either by inadequate workmanship of application or by the coating material, must be rectified by the Contractor at his cost.

The Employer reserves the right to decide when these deficiencies shall be rectified.

The Contractor shall warrant for 5 years for the corrosion protection using high quality coatings with synthetic resins.

#### 1.8.5 Weather conditions for painting

Painting shall only be done when no condensation occurs on the surface. Therefore, relative humidity shall be checked.

Painting of outdoor parts etc. is not allowed immediately prior to and during sand storms, heavy winds and rain.

In hot weather, precautions shall be taken to ensure that the specified dry film thickness of priming or finish coats is obtained.

Any prime coat exposed to excess humidity, rain, etc., before drying shall be permitted to dry and the damaged area of primer removed and the surface prepared and primed again.

The temperature quoted as "normal" in the "Paint System Tables" refers to the climatic conditions encountered at the Qush Tepa and Darzaab Sites.

#### 1.8.6 Surface preparation

General: Surface preparation should remove sufficient foreign matter to allow the type of prime paint used to wet the surface thoroughly and develop adequate adhesion.

In preparing any surface to be coated, all loose paint, dirt, grease, rust, scale, weld slag or spatter or any other extraneous material shall be removed and defects repaired, so as to obtain a clean, dry, even surface to receive the priming or finishing coat(s) as called for in the painting schedules. Sharp edges should be rounded.

All machined surfaces including flange faces shall be suitably covered to prevent damage during surface preparation. All surfaces should be last cleaned whenever possible.

#### 1.8.7 Surface preparation methods

Bare steel surfaces should be prepared by one of the methods described below in order of preference and in accordance with DIN EN ISO 8501-1: 2007 or the Steel Structure Painting Council (SSPC):

- White metal blast cleaning

- Near white metal blast cleaning

- Very thorough mechanical scraping and wire brushing

- Thorough scraping and wire brushing

Mechanical cleaning should only be used when procedures (a) and (b) are not practicable.

In the event of rusting after completion of the surface preparation, the surface shall be cleaned again in the manner specified. Oil, grease, soil, cement, salts, acids or other corrosive chemicals shall be cleaned from steel surfaces by the use of solvents, emulsions or cleaning compounds.

The final wiping shall be with clean solvent and clean rags or brushes. There shall be no detrimental residue left on the surface. Primed areas which suffer damage must be spot blasted on site before touching up.

Protective coating shall be applied as quickly as possible after the completion of surface preparation no matter what cleaning method has been used.

No blast-cleaned surfaces shall be allowed to remain uncoated overnight. Steelworks protected by shop primer after arrival on site shall be cleaned of salt, sand, oil etc. before the first coat of paint is applied on site. Shop primer damaged during transport shall be rectified by blast cleaning and coating before application of the site coats.

Wood surfaces shall be sanded clean. All nail holes shall be puttied and sanded before priming.

Concrete: If a protective coating is required, concrete shall be allowed to cure before painting.

#### 1.8.8 Preparation of coating materials

Primers and paints which have liveried, gelled or are otherwise deteriorated shall not be used. All ingredients in any container shall be thoroughly mixed before use and shall be agitated frequently during application to keep the primer in suspension.

Primer or paint mixed in the original container shall not be transferred until all settled pigment is incorporated into the body of liquid. Primer or paint shall be mixed in a manner ensuring the breakdown of all lumps, complete dispersion of pigment and uniform composition.

Thinners shall not be added to primers or paints unless necessary for proper application according to the manufacturer's instructions.

The type of thinners used shall comply with the manufacturer's instructions. When use of thinners is permitted, it shall be added to the primer or paint during mixing in a well-ventilated area.

#### 1.8.9 Application

Methods: All prime coatings shall be applied by brush or airless spray or a combination of these methods, as approved by the coating manufacturer.

All doors, windows, stairways, handrails (where painted), bottles, flanges and equipment supports shall be finish painted by brush.

Spray guns should not be used outside in windy weather or near surfaces of a contrasting color unless the latter is properly protected from the spray. All cold spray painting shall be done using standard equipment in accordance with accepted industry standards and methods.

Paint misplaced on items that are not to be painted shall be removed on demand of the Employer at the Contractor's expense, leaving the surface clean, unstained and undamaged.

Dry film thickness (DFT): To the maximum extent practicable, the coats shall be applied as a continuous film of uniform thickness and free of pores. Overspray, skips, runs, sags and drips should be avoided. The different coats shall not be of the same color.

Each coat of paint shall be allowed to harden before the next is applied. For epoxy paint, the hardening time before the next coat shall normally be 12-14 hours. Suppliers' recommendations regarding hardening time of epoxy paints shall be observed.

Particular attention shall be paid to full film thickness at edges.

The minimum total dry film thickness of the paint systems shall be as recommended in the applicable "Paint Systems" tables of the technical data sheets. The DFT is given in microns (millionths of a meter).

#### 1.8.10 Protective coatings and paint systems

A color scheme has to be established by the Contractor in cooperation with the Project Manager/Employer. The type and number of protective coats for any item requiring painting on the project shall be in accordance with the "Paint Systems" tables and the Project Manager/Employer's requirements.

Generally, all parts shall receive the specified prime coat(s) at the supplier's works to guarantee that no corrosion occurs during transport to site and storage at site. Parts which cannot be damaged during transport shall receive the full number of coats in factory.

### 1.9 General Requirements for Galvanizing

Galvanizing work shall generally conform in all respects to internationally recognized standards, e.g. DIN EN ISO 12944-5, EN ISO 1461 or equivalent standards, and shall be performed by the hot dip process, unless otherwise specified.

The standards for galvanization shall be the same for both the Qush Tepa Substation and the Darzaab Substation.

It is essential that the shape of steel members and assemblies which are to be hot dip galvanized shall conform to the requirements of the process.

Careful cleaning of welds is necessary before welded assemblies are dipped. The welds and the surrounding metal should be cleaned separately, preferably by sand blasting.

All defects of the steel surface including cracks, surface laminations, laps and folds shall be removed. All drilling, cutting, welding, forming and final fabrication of individual members and assemblies shall be completed before the structures are galvanized. The surface of the steelwork to be galvanized shall be free from paint, oil, grease and similar contaminants.

Structural steel items shall be initially grit-blasted or pickled in a bath, and the minimum average coating weight on steel sections 5 mm thick and over shall be 915 g/m², but not less than 100 micrometers.

On removal from the galvanizing bath, the resultant coating shall be smooth, continuous, free from gross surface imperfections such as bare spots, lumps, blisters and inclusions of flux, ash or dross.

Galvanized contact surfaces to be joined by high tensile friction-grip bolts shall be roughened before assembly so that the required slip factor is achieved. Care shall be taken to ensure that the roughening is confined to the area of the mating faces.

Bolts, nuts and washers, including general grade high tensile friction-grip bolts, shall be hot-dip galvanized and subsequently centrifuged. Nuts shall be tapped up to 0.4 mm oversize after galvanizing and the threads oiled to permit the nuts to be finger-turned on the bolt for the full depth of the nut.

No lubricant applied to the projecting threads of a galvanized high-tensile friction-grip bolt, after the bolt has been inserted through the steelwork, must be allowed to come into contact with the mating faces of the steelwork.

Protecting slings shall be used for off-loading and erection.

Galvanized steelwork which is to be stored during sea transport or at the works on site shall be stacked so as to provide adequate ventilation to all surfaces to avoid wet storage staining (white rust).

Small areas of the galvanized coating damaged in any way shall be restored by cleaning the area of any weld slag and thorough wire brushing to give a metallic clean surface, and by the application of two coats of zinc powder rich paint, or the application of a low melting point zinc alloy repair rod or powder to the damaged area, which is heated to 300°C.

After fixing, bolt heads, washers and nuts shall receive two coats of zinc rich paint. Connections between galvanized surfaces and copper, copper alloy or aluminum surfaces shall be protected by suitable tape wrappings.

#### 1.9.1 Sprayed metal coatings

Corrosion protection can also be achieved by spraying aluminum, zinc, tin, copper, lead or other suitable metals on the surfaces of structures. Composition of coating metals, methods of surface preparation and application of coatings, requirements for thickness and adhesion and subsequent treatment shall conform e.g. to DIN EN ISO 2063 or equivalent.

#### 1.9.2 Weathering steels

The requirements of Standards ASTM-A 242, ASTM-A 588 and EN 10025, DIN EN ISO 12944 or equivalent standards shall be observed in the use of structural steel which is corrosion-inhibited, so-called weathering steels.

### 1.10 Standardization of makes

The works shall be designed to facilitate inspection, cleaning, maintenance and repair. Continuity of supply is a prime concern. The design shall incorporate every reasonable precaution and provision for the safety of all those concerned in the operation and maintenance of the works.

Corresponding parts throughout shall be made to gauge and be interchangeable wherever possible.

All equipment performing similar functions shall be of the same type and manufacture, to limit the stock of spare parts required and maintain uniformity of plant and equipment to be installed at both the Qush Tepa and Darzaab Substations.

The Employer reserves the right to ask for coordination of standardization to the extent reasonably possible, and no price variation will be allowed for this procedure.

### 1.11 Fire protection for materials and for building elements

#### 1.11.1 Fire protection provisions

All equipment, connections and cabling shall be designed and arranged to minimize the risk of fire and any damage which might be caused in the event of fire. Where equipment is normally energized, corresponding precautions, such as fusing, over-voltage or over current protection, shall be provided to avoid risk of fire in the event of excessive current due to a fault on one of the components in the circuit. This is particularly important where voltages are derived from voltage dropping circuits in which failure of a component could lead to the full supply voltage being applied across other components.

Unless otherwise specified or agreed with the Employer/Project Manager, the following design principles shall be observed as minimum fire prevention requirements:

- The stuffing of cable and wall penetrations shall be performed and shall be of incombustible material.

- Cable and pipeline ducts shall be arranged so as to avoid the risk that they will be flooded with flammable liquid.

- Covered floor ducts shall be easily accessible for inspection and cleaning.

- All parts of plant and equipment shall be arranged so that no corners or pits difficult to inspect and clean are formed, where flammable matter could collect.

- For the paneling of walls and ceilings, for floor covering as well as for cubicles and cabinets, incombustible materials are to be used.

#### 1.11.2 Pre-service cleaning and protection of plant equipment

This clause covers mechanical and pre-service cleaning and protection of the plant items and equipment at the Manufacturer's workshop and at site that are not subsequently to be painted.

Cleaning of fabricated component items shall be carried out after fabrication and final heat treatment or welding at manufacturers' works or at site, as appropriate.

In the event of the surfaces not being cleaned to the Employer's satisfaction, such parts of the cleaning procedures or agreed alternatives as are deemed necessary to overcome the deficiencies shall be carried out at the Contractor's sole expense.

Mechanical cleaning, as opposed to alternative chemical cleaning, is the preferred method for workshop cleaning except where this is precluded by design or access considerations.

Machined surfaces shall be protected during the cleaning operations. For re-cleaning small areas, hand cleaning by wire brushing may be permitted. Wire brushes used on austenitic materials shall have austenitic steel bristles.

Austenitic stainless steels, copper and aluminum alloys, cast iron, bimetallic and metallic/plastic items, and components fabricated by spot welding or riveting, shall not be chemically cleaned. All weld areas shall be suitably stress-relieved before chemical cleaning.

All necessary equipment, provisions, chemicals etc. are to be provided by the Contractor.

Besides this, the Contractor shall take over all responsibility for the treatment and disposal of wastes according to the local law and to the satisfaction of the Employer.

The Contractor shall take all necessary precautions to ensure that the internal surfaces of all plant are kept clean and free from injurious matter during erection.

### 1.12 Installation

The switchyard at each of the Qush Tepa and Darzaab Substations shall be designed for outdoor installation as applicable and shall be of the free-standing design, accessible from the front and the rear for operation, inspection and maintenance.

Proposed layout and elevation plans for each switchyard, which shall consider the available space, shall be part of the Contractor's scope. The design shall show recommended clearances for safe operation and maintenance of the equipment and also required lifting clearances for installation.

All components of the switchyard that are connected to earth potential shall be electrically bonded together and connected to a continuous earth bus that extends the entire length of the switchgear. Connecting points for earth conductors from the plant's earthing grid shall be provided at regular intervals on this earth bus.

### 1.13 Steel structures and assembly material

#### 1.13.1 General

Under steel structures are to be understood all substation gantries, building structures and frames, with their body and leg extensions, additional cross arms - if required, the foundation stubs, and stub setting templates.

Under assembly material are to be understood all bolts, screws, rivets, nuts, washers, locking devices which are necessary for the assembly of the steel structures and their accessories as well as for the assembling and mounting of the line equipment like insulator sets, conductor and earth wire accessories.

#### 1.13.2 Steel structures

Generally, the design and stress calculation shall conform to a consecrated code or standard such as DIN 4114 Stress Calculation of Steel Structures, or DIN 18800 Steel Structures; Calculation and Construction.

The local climatic conditions of Jawzjan Province, load calculation, description of loading cases, as well as the applicable design method and safety factors shall be observed as specified in this specification.

The material to be used for the structures is high tensile and mild steel sections and plates, according to internationally recognized standards (ISO 630, DIN 17100 or equivalent).

All structural steel shall be protected against corrosion by hot dip galvanizing.

#### 1.13.3 Assembly material

All necessary bolts, screws, rivets, nuts, washers and locking washers shall be included in the scope of supply of the Contractor with sufficient spare to cover for losses. Members of lattice steel structures including stub setting templates shall be secured by means of bolts and nuts with approved spring washers and lock washers.

All bolts and nuts shall conform to ISO 898 respectively to DIN 267 and shall have metric screwed threads.

Nuts and the heads of bolts shall be of the hexagonal type. Nuts - except lock nuts - shall be full bearing on one side.

Minimum size of bolts for all structural connections shall be 16 mm diameter in mild steel or 12 mm in high tensile steel. The quality of bolts shall not be less than 5.6 according to ISO 898 respectively DIN 267.

All bolts and screwed rods shall be galvanized including the threaded portions. All nuts shall be galvanized with the exception of the threads, which shall be oiled.

Where for any type of tower high tensile steel bolts are employed, then bolts of this type shall be used for all connections for every type of tower on that line in order to avoid the use of mild steel bolts in error where high tensile type should be employed. High tensile steel bolts shall bear a mark on the head to allow identification of grades.

The nuts of all bolts attaching insulator set droppers, U bolts and earth conductor clamps to the towers shall be locked in an approved manner.

All washers shall be included under this contract, including locking devices and anti-vibration arrangements, which shall be subject to the approval of the Employer/Project Manager. Taper washers shall be fitted where necessary.

Nuts shall be finger tight on the bolt and will be rejected if they are, in the opinion of the Employer/Project Manager, considered to have an excessively loose or tight fit. Bolts with threads re-died after galvanizing will be rejected. Nuts and bolts of the same type shall be interchangeable and supplied from the same manufacturer.

When in position, all bolts or screwed rods shall project through the corresponding nuts, but this projection shall not exceed three threads, unless more length is required for adjustment.

The Contractor shall supply the net quantities plus 10% of all permanent bolts, screws, nuts and other similar parts and materials required for installation of the works at each site. Any such assembly material which is surplus after the installation of the equipment has been completed shall become spare parts and shall be wrapped, marked and handed over to the Employer.

## 2. General Electrical Requirements

### 2.1 General

The general electrical requirements specified herein shall be valid for all sections of the technical requirements and shall be followed by the Contractor for both the Qush Tepa and Darzaab Substations.

### 2.2 Voltage levels used in the system

The voltage levels applicable to the Qush Tepa 220/20 kV Substation and the Darzaab 220/20 kV Substation are specified in the schedule of technical data in the Technical Data Sheets (Appendix-1).

### 2.3 Protection class for electrical operational equipment

The switchgear housings shall be designed according to the specified values in the section of technical data sheets.

Additional measures shall consist of sunshades, protection covers against splashing water and additional sealing etc., depending on the particular conditions at each Site.

Free beaming lights in switchgear rooms and lights to be fitted in luminous ceilings for offices and control rooms must be designed at least to class IP 32. The lamps for external lighting and halide lights for internal lighting must have a degree of protection IP 54.

### 2.4 Electrical protective measures

#### 2.4.1 General

The following measures are required for the protection of life, equipment and materials: All parts, i.e. all parts of electrical, operational equipment at an electrical potential above or below earth potential when in operation, and with a rated voltage over 50 V, must be insulated or covered so that they cannot be touched accidentally.

In addition, measures must be taken by the Contractor to prevent the occurrence or persistence of excessively high contact potentials on conductive parts of electrical operational equipment (frames etc.) brought about by faults in insulation.

For installations up to 1000 V, voltages over 50 V are considered to be excessive contact voltages. Within enclosed electrical installations, with voltages over 1000 V, the contact potential shall be according to the values given in internationally recognized standards.

IEC 60079 and IEC 60364, or equivalent standards, apply for installations up to 1000 V. VDE 0101 and 0141, or an equivalent standard, apply for installations above 1000 V and are to be observed in carrying out protective measures and in earthing procedure.

### 2.5 Protective measures for installations up to 1000 V

#### 2.5.1 Protection against direct contact

All "live" parts of electrical operational equipment which can be reached by hand shall be protected against direct contact either by means of insulation or due to constructional design, position or arrangement, or by means of special devices. If, for instance, in case of enclosed switchgear or control cabinets, access is required in the course of normal operation (e.g. for replacing fuses), protection against direct contact must still be ensured when the switchgear cabinet or control cabinet has been opened up, hence all live parts shall be covered.

#### 2.5.2 Protective insulation

Protective insulation is to be provided by means of additional insulation over and above the insulation provided for operational purposes. This measure must prevent the occurrence of a dangerous contact potential.

#### 2.5.3 Use of low voltages as a safety measure

This safeguard applies to all equipment which is required to operate in metallic containers or tanks. The operational voltage of tools and lighting equipment must not exceed 50 V. The isolating transformers shall be installed by the Contractor for the purpose of producing the protective low voltage. A separate 50 V grid will not be provided.

### 2.6 Protective measures for installations over 1000 V

#### 2.6.1 Protection against contact

At least the following measures are to be taken for all parts which are "live" when in operation:

- In general areas: complex protection from all sides against contact; protective devices may only be removed by means of tools.

- In electrical rooms: protection against contact with "live" parts within reach of personnel; protection against accidental contact outside the reach of personnel.

- In enclosed electrical rooms: protection against accidental contact.

The above-mentioned measures for protection against contact are also to be applied to "dead" parts of the plant where, in the case of a fault, a dangerous contact potential might arise, but where, for operational reasons, the parts must not be connected to the protective earthing system.

#### 2.6.2 Protection against contact voltages

Protective earthing is to be used as a safeguard against excessively high contact potentials for conductive parts of the installation which do not form part of the operational circuit. Here, all normally "dead" parts of equipment and apparatus shall be earthed if it is possible for them to come into contact with "live" parts as a result of faults due to the occurrence of surface leakage paths, arcs or direct connections to a "live" part of the equipment.

In considering the dimensioning of the protective earthing system, the thermal loading and voltages on the earthing equipment are decisive factors and should be based on the maximum possible earthing current which can arise.

The earthing equipment and circuits must be of such proportions, as decided by the Contractor, that the contact potential does not exceed the maximum permissible value of 50 V.

#### 2.6.3 Earthing, lightning protection and potential equalizing system

The earthing system and potential equalizing shall comply with the following standards: IEC 60364-4-41, IEC 60479-1, IEC 60479-2, VDE 0141.

For protective earthing, functional earthing, potential equalizing and lightning protection-potential equalizing, a common earthing system shall be established for each of the two Substations.

Within all buildings, internal earthing rings shall be installed. These shall be linked by way of connection tags to the foundation earthing and outdoor earthing system.

All system and plant components that are to be grounded as well as electrical components, like protection and control cubicles, sub distribution boards, control systems, transformers, shall be connected to the earthing bus. All steel structures within a welded section shall be connected to the main earthing system.

No framework parts or other structural components shall be used as earthing bus.

An earthing cable shall be included in all main cable runs. Protective earthing and potential equalizing of electronics cubicles, frameworks, racks etc. shall be executed as follows: earthing rings shall be installed in the relay room and AC/DC room as buses, to be connected at several locations - at least two - to the earthing network. For each row of cubicles, at least two connections shall be made to the earthing ring. Cubicles in a row shall all be connected by conductors to each other.

If cubicles are attached to raised platform flooring of steel structural parts, it shall be ensured that these are electrically connected to each other throughout the area. The raised floor shall be connected to the earthing ring at several locations, and as a minimum at two corners of the room.

Foundation earthing: All buildings, including those with a steel skeleton, shall be equipped with foundation earthing. The foundation earthing shall be installed in addition to reinforcement that is likewise connected together with braided conductors.

The foundation earthing shall be used in connection with the other earthing systems like protective, operational, functional and lightning protection earthing.

In the case of pile foundations, earthing rods of the same length as the piles shall be installed along with the foundation piles at intervals of around 10 m and connected at around every 1 m to the pile reinforcement using braided conductors. The earthing rods shall project beyond the top of the piles and then be connected to the earthing system of the ring foundation.

In addition to the closed ring of the foundation earthing system, a net of a mesh size of about 10 x 20 m shall be embedded in the bottommost concrete layer. The foundation earthing shall be connected to the reinforcement by a braided conductor at intervals of about 3 m.

At intervals not exceeding 20 m, and with at least two in every room, connection tags from the foundation earthing shall be foreseen for connecting the internal earthing ring. Connection tags shall likewise be foreseen for connection to the external earthing system and to the lightning rods.

Optionally, lightning rods can be connected to the external earthing ring, with connections then made from this earthing ring to the foundation earthing by way of the internal earthing ring at intervals not exceeding 20 m.

Screening: The measures described in the following serve for screening and potential control and for lessening overvoltages. For reinforced concrete buildings, at each corner of the building including the bottom slab, an additional mesh of rebars, of about 10 x 10 m mesh size, shall be provided at the topmost reinforcement.

The meshes shall be produced by welding. This additional reinforcement, connected so that it is electrically conducting, may be dispensed with if it is ensured that the existing reinforcement is so connected by welding at appropriate points that it is electrically conducting.

At intervals corresponding to the mesh width, earthing wires from the reinforcement shall be incorporated into the building pillars, rising from the foundations to the roof, and so welded that they are continuous. These earthing wires shall terminate at the roof parapet. The meshes and earthing wires shall be welded to each other.

For steel skeleton buildings, equivalent measures shall be taken. Framework sections shall be welded to make up a defined, electrically conducting connection or shall be bolted together so that they are electrically conducting.

Metal facades and coverings shall be preferred over non-conducting materials and at their topmost and bottommost points shall be connected at an adequate frequency to the lightning protection system.

Reinforcement of cable ducts of reinforced concrete shall be connected to parallel running earthing cables. These earthing cables shall be connected to the screen of the building earthing system or to the foundation earthing system.

Lightning protection: All switchyard and buildings at both Qush Tepa and Darzaab Substations shall be equipped with a lightning protection system.

The building lightning protection system is to be executed in order to offer protection of human life, to prevent damage to buildings and also to the electrical and electronic installations therein.

The lightning protection system shall be executed in accordance with IEC 62305 and other relevant standards, together with the additional measures set out in those standards.

For buildings of a ground area exceeding 40 x 40 m, additional internal lightning conductors shall be laid. Serving for this purpose in reinforced concrete buildings are additional rebars embedded in the building pillars. For steel skeleton buildings, the steel skeleton itself can be used as a lightning conductor, with joints executed so as to be electrically conducting.

Shielding of structures and bonding in side structures shall be in accordance with IEC 81/105A/CDV.

Switchyard equipment earthing: All conductive parts of the installation within the scope of the Contract shall be connected to the main earthing system.

All steel sections or frames shall be provided with at least two earthing straps for every frame or section which is fabricated from parts welded together. The earthing straps shall be located at the ends of the beam section in every case. Screwed connections are considered to be electrically non-conducting.

The Contractor shall provide earthing straps on both sides of the screwed connection and these straps must be interconnected to the main earthing system by stranded copper.

When connecting different materials, the required material transition plates shall, in general, be inserted, in order to ensure that electrolytic action is avoided. All connecting materials shall be corrosion-proof and suitable for the conditions prevailing at the place of installation.

#### 2.6.4 EMC measures

All EMC measures shall ensure that during subsequent operation, no impermissible malfunctions or damage to equipment occurs due to violating electromagnetic compatibility.

The description of the measures is not limited to this chapter, but also forms a part of other chapters, in particular "Protective measures", "Earthing and lightning protection" and "Cabling".

Under consideration of the conditions and constraints, the equipment used shall emit the lowest interference signals and exhibit the highest immunity to interference.

All equipment items shall operate properly when connected to networks with a power supply corresponding to the maximum permissible tolerances as laid down in DIN EN 50178 (as regards harmonics, voltage fluctuations etc.).

In line with general EC regulations for EMC, only equipment bearing the "CE" mark of EC conformity may be used. Priority is given to reducing sources of interference.

Additionally, by means of high-capacity screening, generation of over voltages due to inductive or capacitive coupling shall be reduced. Influencing by electrical and magnetic fields shall be lessened.

Earthing and potential equalizing systems designed for low-impedance shall reduce generation of over voltages due to ohmic coupling.

If EMC resulting from the measures named above is still not adequate, further measures shall be taken within buildings, for example by isolation and suppressor circuits.

Thanks to the lightning protection and screening measures taken at the buildings, within them an EMC protection zone is formed.

All installations penetrating this protection zone, that is where they pass through the external walls of buildings, shall be incorporated into a lightning protection-potential equalizing system as close as possible to the points of entry and exit of the building. This applies also for conductors carrying a potential. At entry or exit, these shall be included in the lightning protection-potential equalizing system by way of suppressor circuits.

Cable runs to outdoor plant components and between buildings may also be screened by appropriate measures, and so form a part of the protection zone. If this is done, the suppressor circuit can be dispensed with.

A suppressor circuit shall be provided at all low-voltage main distribution boards.

Over voltage protection shall be foreseen within the power supply for both central and distributed power supplies to electronic cubicles.

All conductive parts of the structures and installation within the scope of the contract must be connected to the main earthing system.

All steel sections or frames must be provided with at least two earthing straps for every frame or section that is fabricated from parts welded together. The earthing straps shall be located at the ends of the beam section or frame section in every case.

The Contractor must provide earthing straps in front of and behind the screwed connection in every case, and these straps must be interconnected, using stranded copper, and be connected at least at one point to the main earthing system, except the Contractor verifies that the type of screwed connection applied is a permanent electrically conducting one.

When connecting differing materials together, the required material transition plates must, in general, be inserted. All connecting materials must be corrosion-proof and suitable for the conditions prevailing at the installation point.

Each cable tray and cable riser of less than 20 m length has to be earthed once; structures of more than 20 m length have to be earthed twice.

### 2.7 Requirements for local control cubicles and housing for switchgear, control, measurement and signaling equipment

#### 2.7.1 General requirements

If not otherwise specified, the following shall be applied:

Steel clad cubicles and enclosures with fixed, integral switchgear and apparatus must be provided.

The switchgear cubicles must be partitioned off and must incorporate a single busbar system. The necessary instruments, control switches, switch actuators, fuses, switching devices etc. are to be mounted on the front panels of the individual switch and apparatus chambers. The main bus bars are to be installed on the rear face, top side of the switchgear cubicle in a shuttered compartment.

Connections to switching devices, fuses etc. are to be made from these bus bars. The lower part of the cubicle will house the terminal strips and connecting blocks, the clamps for the cable terminals and the required parallel connection copper straps for the connection of more than 2 cables in parallel. An adequate number of earthing clamps must be provided within the switchgear cubicle for earthing the main and distribution bus bars as well as the switchgear itself.

The individual cubicles must be partitioned off from each other by means of an arc resistant and non-smoldering material, e.g. double walls of sheet steel, asbestos-free cement sheets or material of the same properties.

The bus bars must be partitioned off, section from section, by means of arc shields.

The spaces in the interior of the cubicle between the "live" switching element or switchgear element connected to the cable terminals, or between the switch and switchgear parts, must be separated from each other by means of reinforced sheet steel panels, or materials having the same properties.

Care must be taken that in the event of arcing no hot gases escape to the front of the cubicles, i.e. the operational side.

Ammeters are to be provided on the cubicle front panel of each cubicle. A single voltmeter with 4-position voltmeter changeover switch or switchover button must be provided for measurements of busbar voltage between each phase and neutral. Measuring instruments should, in general, be square in shape. Cubicle heating and the required earthing screws are to be provided for each cubicle or cabinet. Cubicle heating for local temperature conditions in all cubicles shall be temperature and humidity controlled. Individual apparatus and devices should be positioned in logical order in appropriate group assembly cabinets. It must be possible in any case to disconnect power supplies to the cabinets by means of manually operated circuit breakers. For easy monitoring and a rapid grasp of the operational state, colored mimic diagrams with the required switch position indicators, apparatus symbols and pilot lamps must be provided in every case on switchgear cubicles.

Plastic insulated, stranded conductors with a minimum cross section of 1.5 mm² must be used for the particular voltage levels: DC control leads; control, measurement and signaling wiring over 60 V; control, measurement and signaling wiring below 60 V (all black); instrument transformer wiring; power cables AC and DC.

Ferrules shall be provided to identify the internal and external wires. R.Y.B. colored ferrules are to be used to identify phase circuits and red ferrules marked "T" for trip circuits.

The terminals must suit at least the following cable core sizes: up to 2.5 mm² for control, measurement and signaling circuits; up to 4.0 mm² for current transformer circuits.

Flush mounted or plug-in type auxiliary relays are applicable. Apparatus being sensitive to impact must be protected against shock and vibration.

All cabinet enclosed switchgear, measurement, control and signaling equipment must be suitable for continuous operation under the climatic conditions prevailing at each installation site. In hand-over state, the cubicles must contain at least 15% of fully fitted spare terminal capacity and 15% of spare space for the future installation of extra equipment.

Incoming and outgoing cables have to be fixed by suitable metallic cable glands, which are to be provided and shall grant the required class of protection.

#### 2.7.2 Color code design for the switchgear, local switching, measurement, control, signaling cabinets and mimic diagrams

Extension equipment supplied by the Contractor shall match the existing color code and symbolic indication system.

#### 2.7.3 Diagrammatic symbols

Diagrammatic symbols complying with IEC 60027, IEC 60034, IEC 60037 and IEC 60117 are to be used for setting out the circuit and terminal layout.

### 2.8 Terminal boxes and terminal cabinets

#### 2.8.1 General

In order to simplify local collection of cables, distribution of signals and to centralize connections in the plant, the terminal boxes or, wherever suitable, terminal cabinets shall be fitted on all the necessary points.

Should the terminal boxes not be adequate, suitable intermediate terminal cabinets are to be used.

#### 2.8.2 Construction requirements

Terminal boxes and cabinets must be equipped with the necessary terminal strips, cable glands, cable screw couplings and attachment components for the connection of the cables. Terminals used for connection of current transformers are to be equipped with short circuit links. The necessary earthing terminals are to be provided for the earthing of the boxes and cabinets.

### 2.9 Power, control and measuring cables and cable supporting structures

#### 2.9.1 Power, control and measuring cables

#### 2.9.2 General construction requirements

MV cables are to be of XLPE copper cable type, LV cables are to be of PVC insulated type. All cables have to be suitable for an ambient temperature of 45°C.

For cables which are subjected to ambient temperature above 60°C, Teflon or silicone insulated cables must be provided.

The cables must be suitable for laying indoor, outdoor (direct or indirect sunlight), in ducts, on trays, underground and in water. The cable sheaths must be resistant to solar radiation, the effect of oil, bacterial action, insects and rodents, in view of the climatic and soil conditions in Jawzjan Province.

All cables must be fitted with a number plate at each end for identification in accordance with the identification system to be approved by the Employer/Project Manager. The individual cores must be identified by numbers or by a color code.

The cables must be laid in such a way that they can be replaced or renewed in a simple manner.

Inside each substation area, cables shall generally be laid on cable trays in reinforced concrete cable ducts. Exceptions are subject to the approval of the Project Manager/Employer. Cables must be carefully arranged and ordered. In locations where proper positioning of the cables is not possible without securing them, quick fastening PVC cable ties must be used.

#### 2.9.3 Cable laying and routing requirements

On vertical runs, walls and ceilings, the cables must be secured with corrosion resistant cable clips (e.g. cable fast layer with protecting cable troughs). In this case two cable clips must be used per meter of cable run, while on horizontal runs one clip per meter is sufficient. More than one cable may only be secured by one clip where it is impossible to lay the cables singly owing to the width of the run.

Cable risers near gangways or in electrical rooms, which are exposed to possible mechanical damage, are to be protected up to 1 meter from ground by suitable metal cover.

After laying the cables, the breaks in the ceiling, floors and walls must be sealed fire persistently. This applies also to switchgear panels and cubicles, to passages between cable ducts, which can be walked through and those which cannot, to vertical runs etc. As there is an increased risk of fire during the construction period, all breaks shall be sealed at least temporarily with fire resistant materials at that stage. This applies especially to vertical runs.

Where the cables are not supported on cable trays or vertical runs, power, DC and instrument transformer cables must generally be run singly in PVC pipes and, where ambient temperatures being expected above 60°C, in galvanized steel conduits. Similar lighting cables, measuring and control cables and telephone cables can be run in one conduit. Surface mounted conduits must be secured every 1.5 m. Generally, cables for double in-feeds from switchgear, distribution boards, cubicles and cabinets must be laid separately so that in the event of a short circuit in one in-feed the other is not affected. They must be thermally independent.

High voltage and low voltage and DC power cables are as a general rule to be laid in separate runs. The cables must be laid in such a manner that they can be replaced or added to without difficulty.

The following minimum separations are to be observed: 300 mm between low voltage power cables and control, measurement and signaling cables for voltages above 60 V; 600 mm between medium voltage cables and control, measurement and signaling cables for voltages above 60 V.

The Contractor has to ensure that adjacent cables do not interfere electrically by using the above-mentioned spacing.

Outside buildings, cables should be laid favorably into cable ducts. If the cables are laid into the ground, after excavating the trench a layer of sand must be filled in. On that layer of sand, the cables are laid, separated from each other according to voltage level. The cables must be laid at a depth of 0.8 m at least, then covered with sand and protected by plastic covers and warning tapes. Finally, the trench is filled with selected backfill. Where cables have to pass under access roads, cable duct blocks and PVC pipe with a suitable bore are to be provided. Cable routes must be marked by cable warning markers.

When laying cables on trays, vertical runs, in cable ducts, etc. and when choosing the size of cables, care must be taken to ensure that adequate ventilation is guaranteed or the cables shall be designed such that there is no risk of thermal overloading, undue pressure or distortion of the cables.

Cables which must move with connected apparatus owing to thermal expansion must be of a flexible type or must have sufficient slack at the location.

#### 2.9.4 Measuring and control cables above 60 V

For voltages above 60 V, these cables must have a minimum conductor cross-section of 1.5 mm². If they lead to outlying buildings, cables with a common core screen and protection against electrical interference must generally be used.

This cable shielding shall exclude extraneous effects and prevent faulty signals generated by adjacent power cables from interfering with the control circuit. For use inside buildings, the shield can be omitted.

Cables with six and more cores shall have black cores identified by white numerals. The numerals shall be printed on the core insulation at intervals not greater than 300 mm throughout the core. The print shall be permanent.

Cable jacket: The cable jacket shall be oil resistant and flame retardant. The cable jacket shall be colored black for all conventional control cables and instrument cables. The cable jacket shall contain the manufacturer's name, cable type and the voltage rating phase to earth/phase to phase in kV.

Cable joints and terminations: Joint boxes should be avoided wherever possible. Any boxes needed are to be made of flame retarding material. Cable branch boxes are not permissible.

When terminal blocks are not available, compression type terminators are to be provided for connecting the cable cores of a cross section of 1.5 mm² upward. In order to strip properly and terminate the cables, corrosion resistant cable clamps must be fixed immediately in front of the stripped cable end.

#### 2.9.5 Instrument transformer cables

Generally, an instrument transformer cable shall transmit the current from only one transformer. If the same voltage is required for different purposes (e.g. protection, measurement, metering), separate miniature circuit-breakers or fuses must be provided within the transformer terminal boxes. The transformer voltages must then be transmitted on different cables.

For instrument transformer cables inside buildings, the minimum conductor cross section shall be 2.5 mm².

Instrument transformer cables from and to outdoor equipment shall have a minimum size of 4 mm² and must generally have a common core screen.

#### 2.9.6 Measuring and control cables below 60 V

For voltages up to 60 V, measuring and control cables shall have stranded or solid copper conductors of minimum 0.8 mm diameter. Multi-pair control cables with paired lay-up of the leads and lay-up of the pairs themselves shall be used. The spare free capacity shall be 15% at least.

Wherever necessary, e.g. for all cables leading outside the relay rooms and/or control rooms, the control cables shall have a common screen (Al foil or Cu foil) to exclude any extraneous effects and to prevent faulty signals.

The individual cores of multi-pair control cables as well as the cable itself shall be identified by code numbers at both ends.

#### 2.9.7 Cable connections and cable joints

For the connections of cable cores with a cross section of 1.5 mm² or larger, compression type cable lugs shall be provided. The terminals shall be designed to ensure that no pinch-off of the cable cores occurs. If cables with a flexible cable core are used, the stripped ends of the cores shall be equipped with a core sleeve before connection. Bimetallic clamps shall be provided in case conductors of different material will be connected.

Where cable ends are stripped, these cable ends shall be attached to the rails with corrosion-resistant clips.

Any cable joints required shall be of plastic material. T-joints are not permissible.

The cable joints used are to be made of low-flammable plastic. When connecting electrical consumers, the cable terminals are to be properly stripped and provided with compression type cable lugs and sealed with glands supplied by the Contractor, establishing durable, reliable connections of good conductivity - the same applies particularly to the protective conductor.

### 2.10 Cable supporting structures

#### 2.10.1 General construction requirements

Basically, pre-fabricated cable trays, cable risers, hanger rods, screws, clamps and all fixing material of corrosion resistant finish, hot-dip galvanized, shall be used. If in certain sections the use of trays and risers is not possible, cable racks are to be provided. These shall be made of corrosion resistant steel angle sections, hot dip galvanized. The steel angles shall be cut to size on site and exposed cut surfaces shall be suitably treated on the spot to prevent corrosion before being fitted. The minimum requirement for this treatment is applying a layer of anticorrosion zinc coating.

All cable tray T-junctions, cross-overs, vertical and other shelving, bends, etc. must consist of pre-fabricated tray elements so that crushing of the cables at these transition points is completely avoided.

The cables laid on the trays shall be carefully arranged and ordered. All cable tray routings consisting of several individual cable trays, which are located outside of buildings and exposed to the sunlight, shall be provided with sunshades made of the material as described for the cable tray equipment.

The trays and risers shall be mounted in such a way that an escape route of at least 800 mm width by 1950 mm height is available for the station personnel in accessible man-ways.

The distance between the individual cable trays and risers shall be large enough to ensure that mutual interference between power cables and instrument transformer, measuring and control cables as well as the cables for the communication systems is avoided. The minimum separations are to be observed.

In outdoor areas the aforementioned cable supporting material shall be provided with an additional coating of plastic. In case of cuts at site the cut surfaces of metal shall be treated with zinc-oxide paint or similar.

Hanger rods for the trays shall be provided at intervals not exceeding 1.5 m so that the maximum deflections specified later are not exceeded. The cable trays shall be jointed in a manner to ensure continuity of electrical conductivity and be connected to the respective substation's earthing system.

For the cables listed below, separate cable trays and cable risers shall be provided: AC power cables above 1000 V; AC power cables below 1000 V; DC power cables; measuring transformer cables; measuring and control cables for 60 V and above; measuring and control cables below 60 V; as well as the cables for the communication systems.

The cable trays shall be designed in such a way that there is 15% spare space on all trays when commissioning and handing over is complete.

The fixing materials for the cable trays and risers shall be corrosion resistant or at least hot-dip galvanized. Rods, brackets and risers shall be fitted with appropriate support brackets to be fixed to anchor rails or fixed by dowels and screws in walls and ceilings. Welding to steel structures and the welding together of hot-dip galvanized cable-laying accessories is not permissible.

For hot-dip galvanized material, a coating thickness of at least 100 micrometers must be guaranteed.

In areas with increased exposure to corrosion, any hot-dip galvanized material used shall be provided with an additional coating, preferably of plastic, with a thickness of 100 - 200 micrometers.

After completion of the cable laying work, the maximum deflection of the cable trays shall not exceed 2.5 mm per 1.5 m (specified distance between two hanger rods).

In exceptional cases, when the prescribed support spacing cannot be complied with, wide span cable trays are to be used. In this case the maximum deflection shall not be exceeded on completion of the cable laying work, as follows:

| Fixing distance (m) | Max. permissible deflection (mm) |
| --- | --- |
| 3 | 3 |
| 4 | 5 |
| 5 | 8 |
| 6 | 11 |

### 2.11 General Requirements for control and monitoring equipment

#### 2.11.1 General

This section covers general requirements for the design of the control and monitoring equipment and, as far as applicable, for interfaces.

The requirements are to be strictly observed with regard to design and execution.

The control and monitoring equipment to be provided shall be suitable for faultless and safe control and supervision of the entire plant during all phases of operation.

As a general rule, measuring points and measuring equipment for interlocking and protection purposes shall be separate and not be combined with measuring equipment for the automatic control equipment. Signals to be processed in several systems, e.g. remote and logic controls, event recording system etc., shall be suitably repeated and mutually decoupled to avoid interaction.

The material of all equipment shall fully meet the requirements regarding safety and operational conditions of the media to be measured. Instrument piping to transmitters and sample piping shall be of stainless steel.

All the equipment shall be suitable for the location in which it is to be mounted and in particular all outdoor equipment shall be suitable for the climatic conditions of the site.

The spare free space capacity of 15% has to be provided for terminals and multi-core control cables.

#### 2.11.2 Control panels, cubicles and racks

Panels, cubicles and marshaling racks shall generally be free standing and shall be constructed of folded sheet steel of adequate thickness to provide rigid support for the control and monitoring equipment which shall be mounted thereon.

Panels shall be mounted on channel base frames. Panels and cubicles designed for personnel access shall be provided with metal floors and shall be suitably ventilated. Doors shall be provided with a lock, which may be opened by a person within the panel without the use of a key. It shall be possible to open all panels associated with one unit by the use of one master key. Adequate lighting and power points for hand tools shall also be provided. The overall height of cubicles, panels and racks housed in the relay room shall not exceed 2.25 m and the color shall be subject to the choice of the Engineer/Employer.

All instruments and control devices shall be easily accessible and capable of being removed for maintenance purposes.

Cable connections to panels and cubicles must be equipped with suitable seals so as to prevent the ingress of dust or vermin or the propagation of possible fires. During installation, sealing of cable penetrations is required.

#### 2.11.3 Cubicles

In the relay rooms, all equipment for voltages exceeding 60 V is to be accommodated in separate cubicles or is to be installed within the cubicles in such a way that a clear separation is achieved and separate connection terminals are used.

Cubicles which are installed in non-air-conditioned rooms shall be provided with temperature and humidity-controlled heating elements. Each thermostat and hygrostat shall have an adjustable set-point, which shall be adjusted during the commissioning period to such a value that no moisture shall occur on the equipment and during periods of high ambient temperature the temperature rating of the equipment is not exceeded.

#### 2.11.4 Marshaling racks

Closed type racks are to be used for the marshaling and termination of low voltage control cables. These shall be constructed of rigid, angle section steel. The height of terminals above floor level shall not exceed 1.8 m. Upon completion of termination, open type marshaling racks shall be enclosed by sheet-metal covers.

#### 2.11.5 Ventilation

Heat dissipation of cubicle mounted equipment shall be kept as low as possible.

Components generating a lot of heat shall be adequately spaced from their mounting boards and from other components.

Natural cooling is preferred. The approval of the Employer/Employer's Representative must be obtained in all cases where it is intended to incorporate forced cooling. If the use of forced cooling cannot be avoided, means shall be provided for indicating and alarming any significant reduction in air flow, and the equipment shall be so protected that no damage occurs due to failure of the forced cooling. The full requirements of the performance specification shall be maintained until the protective device operates. The Contractor shall state how long the equipment can remain in operation at maximum ambient temperature without forced cooling, when submitting the design for approval. Air blown through equipment for cooling shall first be passed through an efficient dust filter. Multi-stage filters, arranged to permit individual filters to be removed for cleaning, are preferred.

The cubicles shall be equipped with high temperature alarm (lamp and potential-free closing contact).

### 2.12 Power supplies and fusing

All monitoring and control equipment inside each substation shall be connected to the auxiliary power supply system.

The Contractor must ensure however that plant mounted equipment is not adversely affected by the long cable runs, particularly to the more distant units.

The main power supply MCB shall be located in functional groups within power distribution cubicles.

The MCB ratings and time characteristics shall be such that in all cases a fault within an individual item or module will cause the MCB associated with that item to rupture and thus disconnect that item from the power supply, before the main MCB is affected.

Failure of a main MCB shall affect the protected zone only and not the entire substation.

Failure of a main control MCB shall be indicated in the control area by means of an alarm. This alarm shall state the identity of the failed main MCB.

Failure of an individual module or component MCB shall be indicated by a general alarm, which shall state the cubicle type in which the MCB has failed, and an individual signal in the respective control module shall be initiated.

The design of the electrical power supplies and protection system must ensure that any faults in modules or other devices, which may block sequence logic interlocks, automatic control systems or other control systems, are restricted to the system in which the fault has occurred.

All electronic devices shall be protected against transient voltage levels which would otherwise damage the device. Drive command modules or devices which take over their function must be separately fused with MCB's.

Interlocks and protection logics for drives can be fused by MCB's together with the drive command module if these logics are used only for the particular control circuit of the drive concerned. Otherwise, they must be fused with the logic of the associated sub-group.

Lamp amplifiers for status indications, alarm indications and criteria call-up (non-fulfilled control criteria) shall be fused by MCB's in groups independently of the logic equipment.

Binary signal conditioning and analogue limit value modules should be fused separately, but may also be fused by MCB's with the corresponding drive control of the drive control level as long as the signals are used only for remote and logic controls (interlocking, protection) of the drive concerned.

When a binary transmitter or limit value is used for several drives or groups, the fusing must be effected separately or be subdivided into logical groups so that any fault arising is confined as far as possible to a drive or group.

All measuring circuits must be separately fused. If the analogue signal will be distributed by analogue signal conditioning and distribution modules, the MCB's shall be located on these modules.

If analogue signal distribution and limit value modules functions are arranged physically adjacent to one another, the limit value modules can also be fused with the corresponding measuring circuit.

All closed loop circuits, including their drives and thyristor controllers, if any, must be fused separately, but if the control circuit fuse fails, the capability of controlling the drive manually must be retained.

### 2.13 Indicators

All indicators mounted on control desks or panels shall be flush mounted. The minimum size for indicators mounted on the various sections of the panels shall be: Non-urgent indicators 96 x 96 mm; important indicators 144 x 144 mm; mimic diagrams preferably 48 x 48 mm.

Indicators shall generally be of the milli-ampere type (0-20 mA). Where digital indicators are used, these shall be provided with at least 4-digit indications. The minimum accuracy tolerance for these indicators shall be 1.5% of span. Indicators mounted on local gauge boards shall be of circular type and shall have a minimum case diameter of 10 mm, preferably 16 mm. All local indicators shall be housed in robust dust and moisture proof cases suitable for open air installation. The read-out window for indicators, recorders and similar equipment shall be non-reflecting, anti-static and minimize parallax errors.

All control instruments shall be rectangular or square type, with the exposed metal portions of all cases having the same finish, trim and general appearance. Instrument and meter scales shall be white with black markings. Instrument cases shall be dust-proof.

Each instrument shall have a zero-adjustment device so that the zero position of the pointer can be adjusted without removing the cover. For frequency measurement purposes it is not permissible to use reed type frequency meters except for the synchronizing equipment.

### 2.14 Switches and relays

Switches mounted in the control panels shall be of the miniature or subminiature type.

The function of the push-button shall be clearly shown. Discrepancy switches or push-buttons shall be provided for the operation of switchgear and the initiation of drives. Discrepancies between the switch position and the plant state shall be indicated by an integral light, which shall illuminate the switch in a flashing mode of operation. Indicating instruments having maximum and/or minimum contacts shall not be used for any main system. All surfaces used for electrical contacts shall be silver, gold or silver alloy. If the Contractor wishes to use other metals, he shall give clear reasons.

The connection between low-voltage electronic control circuits and power circuits shall consist of interposing relays for linking the two systems. All relays have to be of the encapsulated type.

### 2.15 Measurement of electrical parameters

Remote indicators for electrical quantities such as power, voltage, current, frequency, etc. will be of the milli-ampere type.

Solid state electronic type transducers will then be provided to convert the output of current and voltage transformers into an impressed direct current in the range 0-20 mA.

### 2.16 Wiring, cabling terminals

The general requirements for wiring and cabling shall be as specified above. In particular, wiring within panels etc. shall be supported on trays and shall be segregated according to voltage level. Wiring carrying AC and DC voltage shall also be segregated. All panels, cubicles and racks shall be factory wired. Where they must be supplied in more than one section, electrical connections between the sections shall be via terminal strips provided for this purpose.

Spare cores shall be terminated at terminal strips in such a way so as to give a maximum length of core and shall be ferruled in such a way so as to indicate that they are spare cores.

Terminal strips shall be of the screw type. Screw type terminals shall have a metal insert between screw and conductor.

Terminal strips within panels shall be set at an angle to afford easy identification and access.

### 2.17 Labeling and scales

The identification and lettering of scales, dials and inscription, i.e. name plates, labels, etc. shall be in English.

The metric system shall be used for all scales according to the "General Technical Requirements". The identification system as per clauses in the relevant section shall be adopted.

The identification and classification of all measuring points must be shown on diagrams to be produced by the Contractor and entered in the respective lists.

### 2.18 Diagrams, lists and charts

#### 2.18.1 Logic diagram

This kind of diagram shall be used as far as applicable for representation of remote and logic controls and interlocking circuits.

#### 2.18.2 Single line diagram

This is a simplified diagram of the essential electrical equipment and its connections. All circuits are represented by a single line only. In addition, this diagram shall contain all required technical information on the equipment represented, e.g. voltage, ampere, output, code designation etc.

Single line diagrams shall be drawn in a way easy to survey and shall contain as far as possible all technical information of the equipment represented. Except for the general single line diagram showing the basic design and connections, all diagrams shall be prepared according to the classification system.

#### 2.18.3 Circuit diagram

This diagram is resolved into separately drawn "current paths", each showing all its components. The individual circuits shall be drawn in a straight-line sequence.

Wherever applicable, schematic and circuit diagrams shall be combined in one drawing set.

The current paths shall be numbered consecutively from left to right. All switch elements shall be drawn in the de-energized condition. For easy reference, all contacts of contactors or relays shall be completely defined below their corresponding coils. Interconnections to other circuit diagrams shall be clearly marked by means of dotted line separations and the corresponding functional designation.

Circuit diagrams shall also contain all terminals and their correct designations. Terminals grouped together to terminal strips of switchboards, distributions etc. shall be shown on the circuit diagram on one fictitious horizontal line surrounded by demarcation lines.

The representation of electrical equipment and control circuits shall not be terminated at the limits of the scope of supply, but shall be extended beyond this limit by all switchgear, protective measuring and monitoring equipment required for full comprehension of the whole circuit. All terminal and function designations of equipment to be supplied by others shall be included also and marked clearly. This rule shall also apply to the equipment in the scope of the Contractor but of a different nature, like for example power supplies for control panels.

#### 2.18.4 Internal connection diagram

This diagram represents the wiring connections either within one apparatus or between several apparatus of one group. It shall contain the single components or apparatus of one group arranged in the proper positioned order including terminal and terminal strips.

#### 2.18.5 External connection diagram

This diagram represents the wiring connections between groups of apparatus inside an installation or between sections of the installation. External and internal connection diagrams shall always show the full terminal strips with all terminals in the correct sequence.

The terminal connection diagram as described above shall contain but not be limited to the following information: terminal numbers of terminal strip with targets (terminal numbers and current paths) or incoming and outgoing cables; cable designation; type of cable; number and cross-section of conductors; assignment of conductors; number of spare conductors.

#### 2.18.6 Installation diagram

This diagram represents the routing of cables and the position of associated equipment (e.g. lighting fixtures, socket outlets, loudspeakers, telephones, primary elements, transmitters, terminal junction boxes, etc.) according to their correct position in the building plan or arrangement drawing.

#### 2.18.7 Terminal connection diagram

The terminal connection diagram used for terminal boxes, marshaling racks, switchboards etc. shows the terminals and/or terminal strips properly numbered in relation to the incoming and outgoing power and control cables.

#### 2.18.8 Wiring list

The wiring list contains all connections within one apparatus (cubicle etc.) including all terminal numbers to be connected, the wire code and size and the bundle code.

### 2.20 Cable schedule, cable list

The cable lists contain all required information for the design, erection and routing of all power, communication and control cables.

For easy reference, the HV and LV power cables shall be listed in a Cable Schedule containing the following information: all types of cable used; insulation level; operating voltage; all load reduction factors; permissible continuous load of all cables, taking into consideration the various load reduction factors; cross-section of all cables and number of cores; outer diameter of all cables.

In connection with the general schedule, raceway diagrams shall be produced showing routing of cable racks and trays at different elevations, suitably sectionalized and numbered.

#### 2.20.1 Cable list

In addition, cable lists shall be provided for all power and control cables containing at least the following information: cable designation; cable routing (from - to, via raceway); type of cable, cross-section and number of cores; permissible continuous load or burden (for measuring transformers) and load reduction factor; length.

#### 2.20.2 Terminal list

The terminal list contains all connections for a terminal strip of a cubicle on both sides of the terminals, including the codes of wires and cables and their sizes.

#### 2.20.3 Equipment list, device list

The equipment list contains all devices to be installed within one cubicle or apparatus or one group of apparatus, but does not include fixing materials and hardware.

#### 2.20.4 Parts list

The parts list contains all equipment, material and accessories installed in the respective parts of the plant.

## 3. General Requirements Civil Works

### 3.1 Site Construction Works

#### 3.1.1 Contractor's organization

The Contractor shall set up an organization so as to enable performance of the design, construction and tests on completion at the target dates according to the detailed program of work, for both the Qush Tepa and Darzaab Sites.

The Contractor shall submit an organization chart including the key personnel for the period of design, construction and tests on completion.

The Contractor shall revise periodically the organization chart and shall subject it to the approval of the Employer/Project Manager.

#### 3.1.2 Documents for construction site

The Contractor shall prepare and provide in due time, prior to commencement of Construction Works, the following documents which require the approval of the Employer/Project Manager:

- All necessary detailed and approved versions of construction drawings;

- Detailed construction time schedule;

- Site facilities plans;

- Construction site regulations;

- Health and safety plan and regulations;

- Environmental protection plan;

- Quality assurance plan for Construction Works;

- Firefighting and fire protection plan.

#### 3.1.3 Site Store

The site storage area at each of the Qush Tepa and Darzaab Sites shall have sufficient area so that the work process is not jeopardized. It shall be fenced and guarded 24 hours a day.

All materials stored in tiers shall be stacked, racked, blocked, interlocked, or otherwise secured to prevent sliding, falling or collapse.

Maximum safe load limits of floors within buildings and structures, in kilograms per square meter, shall be conspicuously posted in all storage areas, except for floor or slab on grade. Maximum safe loads shall not be exceeded.

Aisles and passageways shall be kept clear to provide for the free and safe movement of material handling equipment or employees. Such areas shall be kept in good repair.

When a difference in road or working levels exists, means such as ramps, blocking, or grading shall be used to ensure the safe movement of vehicles between the two levels.

Material stored inside buildings under construction shall not be placed within 2 meters of any hoistway or inside floor openings, nor within 3 meters of an exterior wall which does not extend above the top of the material stored.

Each employee required to work on stored material in silos, hoppers, tanks, and similar storage areas shall be equipped with personal fall arrest equipment.

Non-compatible materials shall be segregated in storage.

Bagged materials shall be stacked by stepping back the layers and cross-keying the bags at least every 10 bags high.

Materials shall not be stored on scaffolds or runways in excess of supplies needed for immediate operations.

Structural steel, poles, pipe, bar stock, and other cylindrical materials, unless racked, shall be stacked and blocked so as to prevent spreading or tilting.

"Housekeeping": Storage areas shall be kept free from accumulation of materials that constitute hazards from tripping, fire, explosion, or pest harborage.

Vegetation control will be exercised when necessary.

#### 3.1.4 Construction supervision personnel

The Contractor shall provide his own construction supervisory team consisting of: Senior Construction Manager; Construction Manager for Works Sections; Construction Site Engineers of various disciplines; and Construction Inspectors.

The Senior Construction Manager shall be a highly qualified and experienced Manager who represents the Contractor on the Construction Sites (Qush Tepa and Darzaab) in all contractual, organizational and technical matters related to the entire Construction Works.

The Contractor shall prepare an organization chart for the construction supervisory team and submit it, along with job and responsibility descriptions for each position, for the approval of the Employer/Project Manager.

All members of the construction supervisory team shall be nominated in writing. Only the approved persons will be accepted to perform site activities.

#### 3.1.5 Final construction checks

At the end of the Construction Works or of sections or coherent portions of the Works, the Contractor shall on his own perform thorough inspections, tests and checks of these Works with regard to: completeness; defects; and compliance with the Contract and the approved drawings.

The Contractor shall notify the Employer/Project Manager in writing of his readiness to undertake Final Construction Checks and enclose the relevant construction or as-built drawings showing the latest status of the Works. Final Construction Checks shall then be conducted jointly. The results of these checks will be recorded, if necessary deficiency lists will be prepared, and a Final Construction Check Protocol shall be signed.

The Contractor shall remedy without delay the deficiencies of the deficiency list and apply for inspection and signing-off of the deficiency list.

Prior to the commencement of the construction checks on the installation, the Contractor shall submit details of the final construction checks, which also shall prove compliance with the specification, together with the check sheets for each of the items to be inspected, for review and approval by the Employer/Project Manager.

After approval, the Contractor shall perform and record the construction checks, witnessed by the Employer/Project Manager.

After successful completion of the final construction checks, the Contractor shall submit a Report on Final Construction Checks and the Employer/Project Manager shall issue a Certificate of Final Construction Checks, which shall include among other documents the results of the checks including the Deficiency List.

Depending on the result, the Employer/Project Manager may grant or withhold his approval for Commencement of Tests on Completion of this section or portion of the Works.

The Contractor shall remedy without delay the deficiencies of the deficiency list and apply for inspection and signing-off of the deficiency list.

## 4. Inspection and testing of the 220/20 kV Qush Tepa and Darzaab Substations

### 4.1 General

This section contains general requirements for inspections and tests of materials, parts, equipment and workmanship of the Plant during manufacture, assembling and erection and upon completion, to demonstrate compliance with the specification, codes and standards and to ensure overall reliability of Plant operation and performance at both the Qush Tepa and Darzaab Substations.

The Employer, the Project Manager and/or authorized agents shall, at all reasonable times, be allowed free and ready access to the Contractor's premises and those of his suppliers for the purpose of inspecting the specified Plant and Material and obtaining information as to the progress of the work. Failure on the part of the Project Manager/Employer, at this or any other time, to discover or reject Material or Plant or Works which do not meet specified requirements shall not be deemed an acceptance thereof nor a waiver of defects therein.

The approval of the Project Manager/Employer will not prejudice the right of the Employer to reject the Plant if it does not give complete satisfaction in service.

Inspection and testing shall consist of:

- Inspection and tests on raw materials

- Factory tests and inspections: Routine Tests; Type Tests; Factory Acceptance Tests

- Inspections and tests during construction

- Inspections at the end of construction works (Final Construction Checks)

- Tests on Completion

- Performance Verifications

All costs related to the inspection and testing are deemed to be included in the contract price.

### 4.2 Scope, program, documentation

All main components and equipment offered for and supplied under this Contract shall be type tested. The Contractor shall enclose in his Bid Type Test Certificates separately for each such main component and equipment offered.

Such Type Test Certificates shall be issued by internationally recognized testing organizations for type tests carried out on components and equipment which are, in the opinion of the Employer/Project Manager, of identical type or identical in all essential respects to the equipment offered. If any of the Type Test Certificates submitted is not applicable to the component or equipment offered, the Employer/Project Manager reserves the right to require re-testing or the inclusion of additional tests in the routine test program.

During manufacture, erection and after completion, all materials, components and equipment supplied as well as works performed under this Contract may be subjected to inspection by the Employer/Project Manager, should they so require. The works may also be subjected to inspection and tests by any approved agencies of insurance or inspection companies, approved by the Employer/Project Manager, in accordance with the provisions of these technical requirements.

Quality assurance: The Contractor shall provide and operate a quality assurance system both in his facilities and the facilities of his sub-Contractors and at site, capable of producing objective evidence that the material and equipment meet the quality requirements specified. The system shall be in accordance with the ISO 9001 family.

Before delivery to site, a detailed inspection plan shall be submitted to the Employer/Project Manager for approval. It shall describe the facilities and site inspection for each major component and for the finally assembled equipment and shall include the following: a schedule or flow chart indicating each inspection and the stages in the manufacturing and erection process where the Contractor proposes inspection shall be carried out; a short written description of the method for each inspection; standards of acceptance, with references to International Standards or Codes where applicable. Where the Contractor's acceptance standards are proposed, copies of such standards shall be provided.

The Contractor shall have primary responsibility for ensuring the quality of items of equipment supplied under the Contract and remains accountable when manufacture or erection is subcontracted. It shall therefore be a condition of the technical requirements that works are only subcontracted to companies with an effective Quality Assurance (QA) organization and that the Contractor monitors the quality control by the attendance at tests of experienced inspectors employed by the Contractor.

Adequate notice shall be given when the equipment is ready for inspection or test and every facility shall be provided by the Contractor and his sub-Contractors to enable the Employer/Project Manager to carry out the necessary inspection of the plant. A detailed record of the results of all tests and inspections shall be maintained by the Contractor and copies provided to the Employer/Project Manager within a reasonable time after the tests.

Facilities for inspections and tests: The Contractor shall propose detailed programs and procedures for the inspections and tests for individual components as well as for the entire system. The programs and procedures shall be prepared based on the "Quality Assurance System".

The detailed and final inspection and testing programs shall be submitted for the approval of the Employer/Project Manager according to the schedule of documents submittals.

Final notification or confirmation of the inspection or test dates shall be not later than twenty-eight (28) days in advance.

The tests shall be performed to the agreed inspection and test plan using acceptance criteria approved by the Employer/Project Manager.

The Contractor shall provide all the test equipment and test sets required for carrying out the inspection and tests. Equipment provided for testing at site shall remain the property of the Employer.

All equipment shall have current calibration certification.

In the case of Performance Tests, the Instruments shall have been calibrated by an independent calibration authority or institute, the costs of which shall be borne by the Contractor.

The Contractor shall submit test programs for factory and site testing that are subject to approval by the Employer/Project Manager. Test methods shall be based on IEC recommendations and standards. The Contractor shall state the applied standards and test methods. A tentative test program and a test procedure shall be supplied two months before each individual test. The test procedure shall specify in detail the tests to be performed, based on the specified requirements. Detailed documentation (e.g. circuit diagrams, flowcharts) of the tested system/equipment shall also be available to the Employer/Project Manager at the same time. Formats of the test report which are intended to be used shall be submitted for approval together with the test program.

The Contractor shall duly consider provisions specified in the Contract Documents as minimum requirements when preparing the inspection and test plan with respect to type and extent of inspection and tests, to location, orientation and number of test samples, to frequency and amount of taking samples for statistical quality control and with respect to acceptance criteria for all QA measures.

The Employer/Project Manager will return a copy of the Contractor's proposed inspection program indicating those inspection stages for which notification is required. Notification shall be sent at least 28 days prior to the intended test. If the Employer/Project Manager intends to be present at the test, he will provide at least 24 hours' notice and, if his representative does not attend on the notified date, the test may proceed unless an alternative date has been requested by the Employer/Project Manager.

After completion of each and every test, copies of all test records, test certificates and performance curves shall be supplied for all tests carried out in accordance with the provisions of the contract, whether or not the Employer/Project Manager has witnessed them. Information given on such test certificates and curves shall be sufficient to identify the equipment and software to which the certificates refer and shall also bear the Contractor's reference and heading.

The test reports shall indicate the tests performed, contract references, the results obtained, instruments used, names of test personnel, and provide for witnesses' signatures. They shall also be numbered and dated.

The Contractor shall bear the costs for travel expenses for Inspection and Testing.

#### 4.2.1 Rejection of elements

Any item of plant or component which fails to comply with the requirements of these technical requirements in any respect, at whatever stage of manufacture, test, and erection or on completion at site, may be rejected by the Employer/Project Manager either in whole or part as he considers necessary.

After adjustment or modification, if so directed by the Employer/Project Manager, the Contractor shall submit the item for further inspection and/or tests. Plant or components with defects of such a nature that the requirements of the technical requirements cannot be met by adjustment or modification shall be replaced by the Contractor at his own expense and to the satisfaction of the Employer/Project Manager.

### 4.3 Applicable standards for inspection and testing

All equipment shall be inspected and tested in accordance with the requirements of the relevant standards and codes and the present technical requirements and data sheets.

The inspections and tests shall generally be in accordance with the standards used for design, manufacture and erection/construction of the respective Works or parts thereof.

If no appropriate standards are available, inspection and testing shall be made in accordance with the Manufacturer's/Contractor's standard practice.

Test procedures and test conditions shall be sent to the Employer/Project Manager for approval prior to commencement of design of such equipment.

Failure to do so can result in rejection of the tests or even of the equipment or material so tested.

The type and extent of inspection shall generally be in accordance with that specified in the standard used for design and construction of the item of equipment, supplemented or amended by the provisions of the technical requirements.

Additional design tests are also to be carried out as described in the other parts of these technical requirements.

Reference to special codes and standards, where designated either directly or as "relevant", is intended to provide a measure of performance, safety, in-shop and on-site testing, and methods of construction and/or installation which must be equaled or exceeded in order to be considered acceptable for use under these technical requirements. If more than a single degree of quality or accuracy is permitted within the scope of a particular code or standard, the highest quality shall be applicable and the degree of accuracy commensurate with the intended function shall be selected, but with the understanding in either case that the decision as to degree will be made finally along with procedures by the Employer/Project Manager.

In all instances, the finally accepted applicable code or standard shall be the version last published prior to the date of submission of the Bid selected as the basis for this Contract.

Where no appropriate standard is available, tests shall be carried out in accordance with the manufacturer's standard practice, which needs the approval of the Employer/Project Manager. In such cases the Contractor shall submit to the Employer/Project Manager complete data and a suggested procedure for the testing to be performed before manufacture commences. If the proposed procedure is accepted, the Contractor shall provide the Employer/Project Manager with four additional copies in English before any test is performed.

The Contractor's attention is drawn to the climatic conditions in the Qush Tepa and Darzaab site areas. De-rating factors are to be in accordance with the relevant IEC codes and standards or an approved equivalent.

#### 4.3.1 Services prior to and during inspections and tests

In accordance with and in addition to agreed standards, the Contractor shall submit procedures for material testing, manufacture, quality control and performance testing as they apply from the procurement phase of raw materials to the finished product.

No inspection will be made or deemed valid unless the Employer/Project Manager, the Contractor and Sub-supplier are in possession of all relevant approved drawings and procedures for the item to be tested.

The Contractor, on request, shall supply the Employer/Project Manager with a copy of drawings and procedures at the time of the test.

All instruments and apparatus required for the inspection or used for the performance of tests shall be calibrated to an agreed standard at a laboratory of national standing. The cost of making such calibrations shall be borne by the Contractor in all cases.

### 4.4 Test equipment and instruments

Test equipment, apparatus and instruments required for measurement or recording the test results shall be supplied by the Contractor, shall be of an appropriate accuracy, and shall be calibrated. The related costs shall be borne by the Contractor.

In the case of Performance Tests, the Instruments shall have been calibrated by an independent calibration authority or institute, the costs of which shall be borne by the Contractor.

### 4.5 Independent agency

Inspection and testing may be performed by an independent testing agency on behalf of the Contractor. Such an agency requires approval by the Employer/Project Manager.

The Employer/Project Manager may delegate inspections and witnessing of tests to a consultant or to any independent testing agency.

### 4.6 Type Tests

Only type tested electrical equipment shall be provided. The Contractor shall include in the Bid type test certificates for each main equipment item. Only type tested equipment will be accepted.

The Contractor shall present type test certificates issued by an independent institute.

Type tests shall have been carried out on identical equipment by an independent, lawful and reputable, internationally recognized testing laboratory, on all main equipment in accordance with the requirements of the relevant IEC standards.

Equipment type tested shall have the same code/manufacturer/country and equivalent technical parameters as the items offered in the Bid.

In case relevant test data are not available, the Employer/Project Manager may ask these tests to be performed at the Contractor's own expense.

### 4.7 Inspections and Tests during Manufacture

#### 4.7.1 General

As far as practicable, quality of materials, workmanship and performance of all items of the equipment furnished under the present contract shall be inspected at the places of manufacture by the Contractor's QA inspectors.

Equipment shall, wherever practical, be subject to tests on completion in the Manufacturer's works to prove that the reliability, operation and performance conform to the requirements of these technical requirements and the provisions of the appropriate standards.

All facilities shall be provided by the Contractor to enable the Employer/Project Manager to carry out the necessary inspection of the equipment components. The costs of all tests during manufacture and preparation of test records are to be borne by the Contractor.

The Contractor shall submit for approval procedures describing the proposed test methods to be used. Type and layout of test facility, location of instrumentation, formula for calculation of results and correction to site conditions, etc. shall be included where appropriate.

All measuring instruments used in tests shall be regularly calibrated at the expense of the Contractor and records shall be available for examination by the Employer/Project Manager.

The passing of the inspection or test will not, however, prejudice the right of the Employer/Project Manager to reject the equipment components if they do not comply with the technical requirements when erected, or give complete satisfaction in service.

Where the Contractor desires to use stock material, not manufactured specially for the work, satisfactory evidence that such material conforms to the requirements of the Contract shall be submitted. In this case, tests on these materials may be waived, but certificates are to be submitted.

Arrangements shall be made for expediting the shop inspection by having all shop assemblies or pieces covering a single shipment ready at one time. Any packing work as well as transport to the site of the equipment concerned shall not be started before the approval of the Employer/Project Manager has been obtained and all QA certificates due at this time for the equipment concerned have been received and reviewed by the Employer/Project Manager.

Testing of control and monitoring equipment shall comply with all local laws, rules and regulations applicable and be governed by internationally recognized codes and standards.

### 4.8 Test and inspection of materials

#### 4.8.1 General

Materials shall be tested in accordance with the specified standards approved by the Project Manager/Employer.

Unless otherwise specified, the quality of materials shall be verified generally by: chemical analysis (composition, stability by aggressive agents, etc.); mechanical tests (yield point, tensile strength, elongation, etc.); electrical tests (insulation properties, conductivity, resistivity, etc.); thermal tests (thermal constants, thermal stability, etc.).

Non-destructive tests like X-rays, ultrasonic examination, magnetic particle testing shall be applied as much as possible.

Test specimens and samples for analysis shall be plainly marked to indicate the materials they represent.

#### 4.8.2 Workshop assembly

In addition to the quality and production control tests, the following shop assembly work and tests shall be made to check measurements, fitting and functioning.

Equipment to be furnished shall be shop assembled to a status sufficient to prove that the design and workmanship have been executed in accordance with the specifications, that the delivery is complete, and that no work remains to be done at site which reasonably may or should be done in the workshop.

Where applicable, each item of the equipment shall be assembled completely prior to delivery.

Field joints shall be temporarily connected.

All parts shall be properly match marked, identified and doweled to ensure and, where practicable, to facilitate correct and quick field assembly.

If the assembly shows defects in the design or manufacture or unforeseen difficulties in assembling and dismantling, these must be eliminated. If required, design alterations or corrective machining may be executed, provided that no sacrifice with respect to reliability of operation or interchangeability is made and provided that the agreement of the Project Manager/Employer has been obtained.

If the corrections cannot be carried out in accordance with the terms mentioned above, the components concerned will be rejected. The decision on possible subsequent corrections is reserved exclusively to the Project Manager/Employer. Faulted equipment parts shall not be delivered.

#### 4.8.3 Thermal insulating materials

All insulation materials shall be asbestos-free, vermin proof, non-hygroscopic, chemically inert both wet and dry, and fire resistant.

Materials shall be tested for bulk density, specific heat, compressive strength, fire resistance under pressure, and service temperature limit.

#### 4.8.4 Insulated cables and conductors

VDE 0250 - Regulations for cables and flexible cords for electric power and lighting.

VDE 0271 - Regulations for power cables insulated and sheathed with thermoplastic material based on polyvinyl chloride.

VDE 0888 - Optical wave guides for telecommunication and data processing systems.

IEC 60502-1, -2 - Power cables with extruded insulation and their accessories for rated voltages from 1 kV (Um=1.2 kV) up to 30 kV (Um=36 kV).

#### 4.8.5 Installation material

IEC 60335-1 - Safety of household and similar electrical appliances - Part 1: General requirements.

IEC 60364-1

#### 4.8.6 Materials for earthing and lightning protection

The materials for the installation of earthing equipment and lightning protection shall be tested in accordance with the relevant IEC regulations.

### 4.9 Welding and surface coating tests

#### 4.9.1 Welding

For all major structural welded items, the Contractor shall submit the following documented proposals prior to commencement of welding: welding procedure specifications with qualification records; post weld heat treatment procedures where applicable; inspection schedule including quality requirements; non-destructive testing procedures; standard weld repair procedures.

All welders employed on items of plant for this Contract shall be qualified. All welds shall be visually examined and shall be of smooth contour, free from cracks, undercuts and other significant defects. Welds shall be non-destructively tested in accordance with the construction standard applicable to the item of Plant. Where appropriate, magnetic particle testing or ultrasonic examinations are to be applied.

#### 4.9.2 Galvanized zinc coatings

Surfaces shall be visually inspected. Bare patches, lumps, blisters or inclusions of foreign matter shall be cause for rejection.

### 4.10 Primary electrical equipment

Type test certificates issued by an independent test authority shall be submitted.

Testing of electrical equipment shall comply with all local laws, rules and regulations applicable and be governed by internationally recognized codes and standards, which may include, but not be limited to, the following or the latest edition thereof.

The test requirements for primary equipment shall be observed as specified in the schedule of technical data.

Tests for other equipment shall be tested according to the requirements specified below.

#### 4.10.1 Lamps and accessories

IEC 60081 - Double-capped fluorescent lamps - Performance specifications.

IEC 61347-2-8 / IEC 61347-2-11 - Ballasts for tubular fluorescent lamps - General and safety requirements.

IEC 60921 - Ballasts for tubular fluorescent lamps - Performance requirements.

IEC 60155 - Glow-starters for fluorescent lamps.

IEC 60598-2-3 - Luminaries - Part 1: General requirements and tests.

IEC 60188 - High-pressure mercury vapor lamps.

IEC 61347-2-9 - Auxiliaries for lamps - Ballasts for discharge lamps (excluding tubular fluorescent lamps) - General and safety requirements.

IEC 60923 - Auxiliaries for lamps - Ballasts for discharge lamps (excluding tubular fluorescent lamps) - Performance requirements.

IEC 60400 - Lamp holders for tubular fluorescent lamps and starter holders.

#### 4.10.2 Electrically operated tools

The following individual tests are to be carried out on electrically operated tools:

- Each tool must run on no-load at rated voltage and frequency for at least 30 minutes.

- Voltage withstand test at 3000 V during a period of 1 minute: for all insulated tools provided with protective conductor connection.

- Voltage withstand test at 4000 V during a period of 1 minute: for double insulated tools not provided with an earthing conductor.

- Voltage withstand test at 500 V during a period of 1 minute: for tools rated at 24 V, 50 Hz (low voltage protection).

#### 4.10.3 Power installations up to 1000 V

IEC 60364-1 - Electrical installations of buildings.

IEC 60439-4 - Low voltage switchgear and control gear assemblies - particular requirements for assemblies for construction sites.

#### 4.10.4 Protection equipment

Equipment for modular static protection systems (e.g. generator, distance, busbar protection etc.), pre-assembled in the relevant boards/cubicles etc., shall be tested in the Contractor's workshops as far as wiring and proper function is concerned. Simulated inputs (binary signals, current and voltage inputs from test power supplies) shall be used for the tests.

#### 4.10.5 High and low voltage cables

Routine Tests, Special Tests and Type Tests shall be performed according to IEC 60060-1 & IEC 60060-2, IEC 60071-1 & IEC 60071-2, IEC 60230, IEC 60811 and IEC 60840.

#### 4.10.6 Optical fiber cables

Tests shall be performed in accordance with IEC 60793 and IEC 60794.

### 4.11 Control and monitoring equipment

The Substation Control System (SCS) shall be tested according to IEC 61850.

Testing of control and monitoring equipment shall additionally comply with rules and regulations applicable and be governed by internationally recognized codes and standards, which may include, but not be limited to, the following or the latest edition thereof.

All control and monitoring equipment shall be tested at the manufacturer's workshops before dispatch to site.

The Contractor shall submit a comprehensive description of each test for the Employer's approval. This shall include the type and classification of all test equipment and shall be submitted at least two months before the proposed date on which each test is to be carried out unless otherwise specified.

On request, the correct operation of equipment with specified temperature or humidity limits shall be demonstrated by tests conducted within the limits.

#### 4.11.1 Electrical measuring instruments

DIN EN 61010-1 - Specifications for electrical measuring instruments.

IEC 60258 (1968-01) - Direct-recording electrical measuring instruments and their accessories.

IEC 61010-1 - Safety requirements for electrical equipment for measuring, control and laboratory use - Part 1: General requirements.

IEC 61010-3 - Safety requirements for electrical equipment for measuring, control and laboratory use - Part 3: Protocol for the preparation of conformity verification reports for the IEC 61010 series.

#### 4.11.2 Electrical remote indication

VDE 0418 - Regulations for electric integrating meters.

IEC 60338 - Telemetering for consumption and demand.

#### 4.11.3 Calibration tests

The Contractor shall conduct calibration tests of the following instruments and equipment:

- All local indicators over the full range of the indicator

- All transmitters over the full range of the transmitter

- All binary transmitters over the full range including initial setting

- All analogue limit modules, function generators, flow evaluators

- All remote indicators over the full range of the indicator

- All recorders over the full range of the recorder

- One of each type of indication loop with circuit resistance of the loop increased to a value which is equal to the highest value expected, and under worst case operating conditions

- One of each type of thermocouple or resistance element

- All modules and subassemblies for measuring and control, e.g. analogue limit monitors, flow evaluators, function generators

- All quantity meters

- All synchronizing units according to IEC standards

### 4.12 Telecommunication equipment

#### 4.12.1 General

Factory tests shall not begin without the prior delivery and approval of documentation for test procedures.

The communication system shall be tested according to all relevant parts of IEC 60870.

Special care shall be taken for the interfaces with the SCS equipment as well as the telephone and radio system.

#### 4.12.2 Tele-protection equipment

Equipment and system performance testing according to IEC 60834-1 and IEC 60834-2 shall be performed. In addition to IEC 60834-1, Clause 20, a measurement of transmission time shall be performed.

#### 4.13.3 Check tests on structures

The testing of material specimens to establish whether the materials used in the structures comply with the specification for structural material is as described in the individual technical Specifications.

The types of check tests described hereinafter are applicable to the finished parts of the structure. They may be used in routine inspection and for quality control.

If the results of the check tests show that the quality of the materials is inadequate or if other defects are revealed, the Project Manager may require a loading test to be made.

Type of check tests: cutting cores, the procedure used shall comply with the requirements of DIN 1048, Part 2 or of an approved standard; gamma radiography, the testing shall be carried out in accordance with the requirements of an approved standard; ultrasonic test, such tests may be used to obtain approximate indications of the strength of the concrete in the structure; electromagnetic cover measuring devices, such tests may be used to verify the position of the reinforcement and shall be in accordance with the requirements of design; rebound hammer test, such tests may be used to obtain approximate indications of the strength of the concrete.

#### 4.13.4 Load test on structures or parts of structures

The Project Manager shall instruct the Contractor to make a loading test on the Works or any part thereof if in their opinion such a test is necessary.

For the purpose of testing floors, roofs and similar structures and their supports, the test shall be equivalent to one-and-a-quarter times the live load for which the works or part thereof to be tested have been designed.

Wherever certain procedures for testing of parts in structures (e.g. piles) are required by standards or codes of practice, these are to be followed. All tests must be conducted in the presence of the Engineer/Project Manager.

For a test on a floor, roof or similar construction, the result shall be deemed to be satisfactory if, upon removal of the load, the residual deflection does not exceed one-quarter of the maximum deflection after maintaining the load in position for twenty-four hours. If the residual deflection exceeds this amount, the test shall be repeated, and the result shall be deemed to be satisfactory if the residual deflection after removal of the load for the second time does not exceed one quarter of the maximum deflection occurring during the second test.

If the result of the test is not satisfactory, the Project Manager/Employer shall instruct that the part of the Works concerned be taken down or cut and reconstructed to comply with this Specification, or that other measures be taken to make the Works secure. The Contractor shall at his own cost take down or cut out and reconstruct the defective work or shall execute remedial measures as instructed by the Employer or the Project Manager.

### 4.14 Inspection and testing during erection for the substations

#### 4.14.1 General

The Contractor's scope of delivery includes all site test and inspection expenses, e.g. all labor, materials, water, electricity, consumables, chemicals and stores, as well as the instruments and apparatus as may be required to perform such tests efficiently, at both the Qush Tepa and Darzaab Sites. The Contractor is responsible for and shall include in his delivery all safety measures such as barriers, warning signs etc. required for inspection and testing while erection is in progress, and all interruption of work in this connection will be at his expense.

The Contractor is responsible for ensuring that safe procedures are adopted for the use, handling and storage of radioactive sources and an inventory of all sources supplied to each site shall be maintained.

All instruments and apparatus used for site inspection and testing shall be calibrated to an agreed standard at a laboratory of national standing to be nominated by the Contractor. The cost of making such calibrations shall be borne by the Contractor in all cases.

During the erection of all mechanical, electrical, control and monitoring equipment as well as during the civil construction, the Contractor shall make the Plant items available at any reasonable time for inspection by the Project Manager and/or by the Employer, should either so require. To assist the Employer and the Project Manager in their review of the quality of the work being performed, the Contractor's senior field representative shall provide the Project Manager/Employer with a schedule of the specific areas and items of work that will be performed during each work week.

All work that is executed without notification shall, at the Project Manager's/Employer's option, be subject to removal and replacement by the Contractor at his expense.

In particular, the Contractor has to mark on his implementation schedule all stages of erection or commissioning which are subject to the Project Manager/Employer's acceptance and has to notify one week in advance when such acceptance becomes due. The stages subject to acceptance shall include but not be limited to the items indicated in this Specification.

The Project Manager's/Employer's written approval of completed work stages shall be obtained before continuing with erection, and should it be necessary to dismantle subsequently erected parts in order to gain access for inspection or rectification, this shall be at the Contractor's expense and no claim by the Contractor for delay shall be considered.

The following checks and tests/measurements for each substation shall be made during erection unless otherwise specified in this specification (as appropriate) in accordance with agreed standards:

- Checking for complete delivery

- Cable route and laying depth inspection, special filling resistance tests

- Screwed connections for correct assembly

- Terminals and terminal connections for correct assembly

- Checking of earthing connections and testing of earthing resistance

- Measurement of insulation values

- Fire-proof partitioning

- Marking, inscription, provision of designation plates, safety signs and warning signs

- Setting of indicators

- Checks on wiring and cabling for conformity with the constructional circuit-drawings and plans

#### 4.14.2 Earthing system resistance measurement

The earthing system resistance shall be measured during initial installation and immediately before commissioning, but at least once during the dry season under reasonably dry soil conditions.

The measurements are to be carried out by means of a high frequency earth resistance measuring instrument, in order to allow readings of the impulse resistance value of the earthing system.

The measurement shall be performed with the earth wires from OHLs disconnected.

The measurements have to be clearly recorded. The schedules used for the recordings shall contain, in addition to the measured ohmic values, details of the surface soil and underground data at the time of tests as well as the soil resistivity values.

#### 4.14.3 Galvanizing thickness

The galvanizing thickness shall be tested on site after receiving the galvanized components as well as during erection. The zinc coatings shall comply with the thickness requirements defined above.

The Contractor shall have available on site for the Project Manager's/Employer's use an instrument suitable for the accurate checking of galvanizing thickness, available from the time of arrival of the first consignment of steelworks until the issue of the taking over certificate. The cost of the gauge and other operating expenses are deemed to be included in the Contract Price.

If evidence of white rust is apparent upon receipt at site of bundled steel section, the Project Manager/Employer shall order the Contractor to make such tests as he deems necessary to determine the extent of damage, if any, and the remedial measures necessary.

### 4.15 Tests on completion for the substations

#### 4.15.1 General

After Final Erection Checks, the Tests on Completion shall be performed.

The Tests on Completion comprise: the cold commissioning tests, which are the tests to be performed on each individual item of Plant without having the control voltages in operation; the hot commissioning tests, which are the tests to be performed with the control voltages in operation and include the tests on different subsystems and systems; energization, which includes the tests performed during the energization of each substation; and tests after energization, which include tests to be performed with the substations energized.

#### 4.15.2 Cold commissioning tests

The cold commissioning tests comprise the tests to be performed as site tests for the individual primary equipment items.

#### 4.15.3 Hot commissioning tests

The hot commissioning tests comprise mainly the tests of subsystems and systems, but not limited to the following:

- Establishing the AC and DC control voltages and the relevant tests

- Local control of the 220/20 kV equipment, interlocking

- Startup of the substation control system, remote control of all equipment

- Tests of the protection relays

- Tests of the communication equipment, checking correctness of measurements

- Testing the air conditioning system

- Measurement of the earthing resistance of the substation

- Other tests as may be required by the Project Manager/Employer

#### 4.15.4 Energization

The tests during energization comprise mainly but are not limited to:

- Energize all 220/20 kV equipment

- Check correct voltage and current measurements

- Synchronization tests of CBs

- Checking the direction of phase rotation

- Checking the operation of the voltage regulators of the power transformer

- Testing the functionality of the protection relays

#### 4.15.5 Tests after energization

The tests after energization comprise mainly but are not limited to the following:

- Stability tests of the protection system

# Chapter 04

# 220 kV Outdoor Switchyard

## 1. 220 kV Outdoor Switchyard

This section of the Specification covers the technical requirements for the 220 kV outdoor switchyard of the Qush Tepa 220/20 kV Substation and the Darzaab 220/20 kV Substation, developed under the Electrification of Qush Tepa and Darzaab Districts Project of the Ministry of Energy and Water (MEW) of the Islamic Emirate of Afghanistan (IEA), Jawzjan Province.

This specification shall be read together with the drawings attached in Appendix-2 and with the Schedule of Technical Data in Appendix-1.

### 1.1 General

The requirements specified under section General Technical Requirements B0.2 shall apply, where applicable, together with the further regulations of the other sections of this specification.

All materials and equipment delivered and installed shall be brand new, of the manufacturer's normal and standard construction, designed and manufactured according to the latest technological methods, and suitable for outdoor operation under the ambient conditions specified for Jawzjan Province, including high summer ambient temperatures, dust and seismic considerations.

The Contractor is responsible for ensuring that all relevant safety requirements are observed closely during manufacturing, transportation, assembling, erection, testing and trial operation until the Contractor's responsibility under the Contract ends.

Radio Interference Voltage (RIV):

All equipment shall be designed and constructed so as not to cause interference with radio reception or telephone communication circuits, in accordance with modern practice and IEC 60694. The limit of radio influence voltage shall be 500 microvolts for each item of equipment, measured in accordance with IEC 60694.

### 1.2 Equipment supports, gantries and other steel constructions

All equipment supports and other steel constructions shall be calculated according to IEC 60826 and designed and erected according to the current editions of IEC 60694 as well as EN 50341 or other relevant equivalent standards, considering the local design conditions and a safety factor of 2.0.

Rolled steel sections, flats and plates used shall not be inferior in strength and quality to those specified as St 37 and St 52 in DIN 17 100.

The Contractor shall prepare the loading tree for the different structures, considering all forces acting on the structures including the required safety factors. The data from the loading trees shall constitute the input for the calculation of profiles, bolts, etc. Calculations shall be performed using professional software approved by the Project Manager, and the results shall be transposed into assembly and shop drawings for approval.

#### 1.2.1 Galvanizing

Except where specified otherwise, all iron and steel used in the Works shall be hot-dip galvanized. The minimum weight of galvanizing coat shall be: 900 g/m² (100 micrometers) on steel sections 5 mm thick and over; 600 g/m² (80 micrometers) on steel sections 2–5 mm thick; and 500 g/m² (70 micrometers) on bolts and nuts including the threaded portion. The zinc coating shall be smooth, clean and of uniform thickness, and free of defects. All drilling, punching, cutting and bending shall be completed and all burrs removed before galvanizing.

#### 1.2.2 Material requirements

Fabrication of steelwork shall prevent any irregularity that might cause difficulty in erecting the gantries and structures on site. All members shall be secured with bolts and nuts fitted with plain and spring washers; the diameter of mechanically stressed bolts and nuts shall not be less than 12 mm with metric threads. Bolt heads and nuts shall be hexagonal, minimum quality 5.6 per DIN 267. Built members shall be true and free from links, twists and open joints.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

### 1.3 Bus bars

For the 220 kV double busbar configuration, the busbar type and size shall be selected according to the design. Spare conductor with clamps and connectors, complete with all required accessories, shall be provided for both busbar and equipment connections.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

Additionally, the Bidder shall submit a calculation demonstrating that the chosen cross-section is sufficient for the required rated current.

### 1.4 Equipment connections

Equipment connectors shall be designed as AAAC conductors. All hardware such as connectors, joints and clamps shall be designed for the specified AL conductor and shall be of the compression type; bolted clamps may be used only where compression clamps cannot be manufactured. All connectors shall be of aluminum with a current-carrying capacity and strength equal to or greater than the buses they serve, and shall be practically free from copper.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

### 1.5 Overhead conductors

The conductor type shall be AAAC with adequate cross-section for the specified rated and short-circuit currents.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

### 1.6 Ground wires

For lightning protection, ground wires of galvanized steel type shall be installed throughout the outdoor switchyard.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

### 1.7 Post insulators

Insulators shall be of the outdoor, solid-core station post type, conforming as a minimum to IEC 60168 and IEC 60273. Porcelain shall be manufactured by the wet process and shall be one piece, non-porous, homogeneous and free from cavities or other flaws. Glazing shall be uniform in brown color and free from blisters, burns and other defects.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

### 1.8 Insulator units, string insulators

For supporting overhead connections, cap-and-pin type glass string insulator assemblies shall be used, assembled from string insulator units. The creepage distance shall strictly follow the local design conditions specified for Jawzjan Province. The electrical and mechanical design shall comply with IEC 60071, VDE 0210, IEC 60383 or other relevant equivalent standards.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

### Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

In addition, the Bidder shall submit the number of failures of units/strings per year for the last 10 years.

### 1.9 Circuit breaker

#### 1.9.1 Technical requirements

The manufacturer shall guarantee the maximum over-voltage factor and all other electrical values according to IEC 62271-100 and other relevant IEC/VDE standards. The device shall be clearly labelled 'ON' and 'OFF'. The circuit breaker used in line feeders shall be suitable for single-phase, single-shot rapid auto-reclosing with enabling/disabling function.

All circuit breakers shall be capable of an O-CO switching cycle when the auxiliary voltage is lost. The driving mechanism shall be of the spring-operated type, of the trip-free design, with manual emergency operation mounted separately from live parts.

The breaker shall be equipped with a temperature-balanced, remote and locally indicating two-stage SF6 gas monitoring system. The circuit breaker shall be designed on the single-pressure (puffer) principle, with the possibility to replenish gas while in service. Portable SF6 gas bottles with accessories, plus spare bottles, shall be furnished by the Contractor.

#### 1.9.2 Local control cubicle

The cubicle housing the operating mechanism shall accommodate the auxiliary contacts, shunt trip coils for 'ON'/'OFF' operation, the terminal block and the local/remote control devices. The cubicle shall be of protection class IP 54, equipped with a 230 V heating element and a hygrostat, interior LED lighting operated by a door switch, and a 230 V/10 A single-phase outlet. A copper earth busbar with tapped holes shall be provided and connected to the shields of all incoming cables.

Terminal blocks shall have sufficient spacing, with at least 20% spare terminals per block. All internal wiring shall be neatly trunked and identified at both ends. Operation and fault-operation counters shall be installed, and all circuit breakers shall be designed for closing/tripping from both remote (substation control room) and local electrical controls via a LOCAL/REMOTE selector.

Operation of the breaker shall be actuated by two independent trip coils and one close coil, with duplicated and automatically supervised trip circuits. DC power supply, trip coil and control circuit wiring shall use shielded cable (e.g., type NYCY).

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

### 1.10 Isolators and earthing switches

Isolators shall be of the centre-break type, mounted on a common support and operated three-phase by a common motor-driven operating mechanism, mechanically coupled to ensure synchronism of all poles. Isolators shall be designed for the specified rated currents, suitable for off-load isolation and capable of withstanding the specified short-circuit forces. Manual emergency operation shall be possible.

All isolators shall be electrically interlocked with the corresponding circuit breaker and with the associated earthing switches, such that the isolator can be closed only when the earthing switch is open, and vice versa. Line earthing switches shall additionally be interlocked with a no-voltage relay connected to the line voltage transformer, indicating a dead overhead line.

Local control cubicles

The local control cubicles shall house the motor-driven operating mechanism, permit manual operation by handle, and be equipped with local/remote selector switches, terminal blocks, earthing poles, flexible earthing connections, metallic cable glands, humidity-controlled heaters, a 16 A outlet and door-controlled lamp, in accordance with the requirements for circuit breaker cubicles specified above.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

### 1.11 Voltage transformer

General Requirements

The rated burden of the protection cores indicated in the data sheets shall be considered as the minimum requirement for all possible ratios; the Contractor may select either primary reconnection or secondary taps to achieve the specified ratios. The Contractor is responsible for defining the final characteristics of the CT and CVT cores for protective relaying so as to satisfy the performance requirements of the offered relays, subject to the Employer's approval prior to manufacturing.

Means for checking the integrity of CT and CVT circuits shall be provided, either automatically or manually, without inhibiting the protection function. The CT and VT terminals of the relay panels shall be equipped with links for interrupting/shorting and with measuring points; each current transformer circuit shall be earthed through a single link.

Voltage transformer ratio (capacitive voltage transformer, one winding open delta): 220/√3 kV / 110/√3 V / 110/√3 V.

#### 1.11.1 Technical Requirements

Capacitive voltage transformers shall be installed in all 220 kV feeders as indicated on the single line diagram, of single-phase type, one end of the primary winding directly earthed, with metallic diaphragm seal, installed on separate supports. An electronic fast damping device shall be provided to damp transient and ferro-resonant oscillations. Fuses shall protect the secondary winding, and windings shall be designated per IEC standard.

#### 1.11.2 Control box

The control box shall house adequate terminals of the secondary windings, marked per IEC standard, with adequate heaters against humidity and suitable metallic cable glands.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

### 1.12 Current transformer

General Requirements

The current transformers shall have 5 secondary windings and shall be made in tropical export version. Current transformers shall preferably be of the low-reactance type. Performance shall not be inferior to that defined in the applicable IEC publications. For class 'X' type, the knee-point voltage shall be established for each possible ratio, considering maximum short-circuit conditions, actual secondary winding resistance at 75°C and 150% of the anticipated external burden, with magnetizing current at knee-point not exceeding 5% of the nominal secondary rated current.

#### 1.12.1 Technical requirements

Current transformers shall be of oil-immersed, outdoor type, provided with oil level indicator and expansion compartment, single-phase, installed on separate supports. The Contractor shall provide calculations demonstrating that the offered protection functions correctly with the offered current transformers under actual short-circuit conditions.

#### 1.12.2 Control box

The control box shall house adequate terminals of short-circuit type for current transformers, marked per IEC standard, with adequate heaters against humidity and suitable metallic cable glands.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

### 1.13 Surge arresters

Surge arresters shall be of the gapless zinc-oxide type, installed on separate supports in all 220 kV line feeder bays close to the lines, and near the transformer bushings. They shall be hermetically sealed, ensuring permanently reliable performance irrespective of ambient conditions, and shall comply with IEC 60099-1/5 and relevant equivalent standards. The impulse spark-over voltage shall be higher than the power-frequency spark-over voltage but lower than the impulse test voltage of the switchgear. Each arrester shall be equipped with a pressure relief device and a surge counter of enclosure type IP 54, installed in the earth conductor.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

# Chapter 05

# 220/20 kV Power Transformer

## 1. Power Transformer

### 1.1 General

This section of the specification covers the technical requirements of the 220/20 kV power transformer(s) for the Qush Tepa Substation and the Darzaab Substation.

### 1.2 Power transformer

These technical requirements shall be considered together with the attached Schedule of Technical Data, Appendix-1.

### 1.3 Technical Requirements for the Power Transformer

#### 1.3.1 Required Technical data

The technical data for the transformer(s) are specified in the Schedule of Technical Data, Appendix-1.

#### 1.3.2 Test requirements

The test requirements for the power transformer(s) are specified in the Schedule of Technical Data, Appendix-1.

#### 1.3.3 Magnetic cores

Cores shall be constructed from cold-rolled grain-oriented transformer steel sheets, clamped strongly enough to prevent displacement under short-circuit or other stresses; the clamping frames shall be insulated from the sheets. Where the Contractor can demonstrate no adverse effect from core or stray-flux heating, flux density under the most onerous conditions shall not exceed the specified value.

#### 1.3.4 Windings

Copper windings of excellent-quality insulation shall be used, supplied to IEC insulation class A. Insulation shall be protected against mould and other tropical effects, tropicalized per DIN 40040 or an equivalent standard, and thoroughly seasoned during manufacture by axial pressure at elevated temperature to prevent further shrinkage in service. Windings and leads shall be braced to withstand shocks from transport, switching and other transient conditions. Internal earthing of the magnetic circuit shall be made through a removable link accessible beneath an inspection opening in the tank cover.

#### 1.3.5 Tank

The transformer tank shall be designed to the applicable IEC standard, with four jacking points rated for the most unfavorable load distribution, four lifting hooks for crane lifting, and 4 transport rollers each capable of 90° rotation without dismantling. The tank cover shall be of adequate strength, fitted with suitably spaced bolted flanges and inspection openings, designed to avoid external water pockets and internal air pockets. Interior surfaces shall be coated with an oil-resistant paint; exterior surfaces with a primer and two finish coats. Pockets for dial-type thermometers shall be provided at the position of maximum oil temperature, with caps to exclude water ingress. Two earthing screws shall be provided at the lower tank frame.

The conservator tank shall be arranged above the highest point of the circulating system, with connections at the highest point to prevent trapping of air/gas under the main tank cover. Its capacity shall be adequate for the expansion and contraction of oil under the specified operating conditions and shall be fitted with a filling cap, drain valve with captive cap and oil level gauge. A silica-gel air dehydrator, sized for the local climate of Jawzjan Province, shall be fitted to the conservator.

#### 1.3.6 Rails

Rails shall be provided for supporting the power transformer(s); steel quality shall be at least St 37 per DIN 17100 or an equivalent standard.

#### 1.3.7 Bushings

The transformer shall be equipped with top-quality bushings on both the 220 kV and 20 kV sides, complying with the relevant IEC standard, arranged upright on the tank cover and easily exchangeable without lifting the cover plate.

#### 1.3.8 Cooling

The transformer(s) shall be designed for ONAN/ONAF cooling and equipped with detachable, flanged radiators designed to permit easy cleaning and painting and to avoid water pockets, capable of withstanding the pressure test. Each radiator group shall include a drain valve, air release plug and sufficient cooling fans, with shut-off valves at top and bottom connections to permit radiator removal without the temperature rising above permissible values while in service.

#### 1.3.9 On-load tap changing

Winding taps shall be provided as specified in the Schedule of Technical Data. On-load tap changers (OLTC) shall comply with the specified IEC standard and be suitable for power flow in both directions, of a type test verified in accordance with that standard, and suitable for oil change without dismantling the diverter unit. Tap selectors with make-before-break switches shall be housed in a separate compartment integrated in the transformer tank, with its own pressure relay and separate oil system. Contacts shall be designed for a service life of approximately 200,000 operations under rated load.

The tap changer shall be designed for supervisory, normal remote and local emergency control, with a lockable gear, housed in a suitable weather-, vermin- and insect-proof cubicle with humidity- and temperature-controlled heating. The tap-changer assembly shall include a pressure relief device.

The on-load tap selector controls shall satisfy the following: the electric drive shall not be operable when the manual operating gear is in use; the control switch shall cause only one tap movement unless returned to the off position between operations; all controls shall be clearly labelled to indicate the direction of tap changing; and it shall be possible to operate manually, with individual AVR, or by parallel operation.

The cubicle shall provide as a minimum: a lamp indicating tap-changer operation; door-switch controlled illumination; a 230 V/16 A socket; and a temperature/humidity-controlled heating element. Outside the cubicle, visible from the maintenance road, indication of the tapping in use, the number of operations completed, and a manual emergency drive operated by handle shall be provided. The driving motor shall be rated for the specified voltage with thermal/overload protection, operable at voltages down to 20% below rated voltage, and fitted with limit switches and mechanical stops to prevent over-running.

#### 1.3.10 Transformer oil

Transformer oil shall be pure mineral oil, free from additives, acid-refined per the appropriate IEC standard.

#### 1.3.11 Noise limits

The transformer shall be designed and constructed such that harmful vibrations are eliminated and minimum noise occurs at any operating condition; it shall pass the specified noise level test.

#### 1.3.12 Protection

Besides the protection relays installed in the control room, the transformer shall be protected by: a Buchholz relay with slide valve to enable dismantling without oil leakage; a dial-type thermometer for oil temperature control with two adjustable maximum contacts (60 °C–120 °C range); oil level indicators with low-oil-level contact; and a resistance-type thermometer (R = 100 Ω) for winding temperature control.

#### 1.3.13 Transformer neutral

The neutral of the power transformer shall be brought out to a bushing.

#### 1.3.14 Transformer losses

A guarantee shall be given that the transformer losses indicated in the Schedule of Technical Data are not exceeded. Tolerances shall apply in accordance with the specified IEC standard, and a penalty shall apply only if these tolerances are exceeded.

Rejection

The Employer shall have the right to reject any transformer if the actual values exceed the guaranteed values, including IEC 60076 tolerances, by more than the following margins: no-load losses +15%; load losses +15% total losses; rated power −5% for +10%; impedance voltage on main tapping ±5%; impedance voltage on extreme taps ±10%.

#### 1.3.15 Indicating plates

Rating, diagram and general-plan plates, as specified in IEC 60076 including space for the Employer's serial number, shall be mounted on the low-voltage side of the tank at about 1.5 m above ground. Inscriptions shall be in English.

#### 1.3.16 Piping and valves

Piping for connection/filling of the various transformer parts and valves for oil sampling, draining, filtering and venting shall be included; drain valves shall accept suitable adapters for direct connection of oil sampling hoses.

#### 1.3.17 Cabling and wiring

Cables from supervisory equipment to terminal boxes shall be heat resistant, steel-armored and rigidly fastened to the tank, with stranded copper wiring, slip-over ferrules and crimped terminations. Minimum wiring cross-section shall be 2.5 mm². Alarm and trip wiring shall include an insulated green/yellow protective earth conductor of at least the same cross-section as the line conductor; grounding conductors shall not be less than 16 mm² and shall be green/yellow colored.

#### 1.3.18 External cabling

Cables from the control room to the transformer control boxes shall be steel-armored or special heat-resistant cables in metal pipes, fixed to the transformer.

#### 1.3.19 Marking and labeling

All parts of the transformer shall be completely labelled, clearly legible at all times, marked per VDE 0532 or a similar standard. Weather-exposed labels shall be enamel type; labels not directly weather-exposed shall be light-resistant, non-fading and scratch-resistant. All labels and markings shall be in English.

#### 1.3.20 Corrosion protection, painting

The main tank shall be spray-galvanized and painted; the conservator tank, radiators, control and monitoring cabinets shall be hot-dip galvanized, treated externally and internally with an oil-resistant coat. The external paint shall consist of 4–5 layers, total minimum thickness 200 micrometers.

#### 1.3.21 Voltage regulation

An electronic voltage regulator (AVR) shall be supplied, suitable for voltage regulation without hunting, installed in the control board, meeting minimum requirements comparable to: sensitivity 0.4–6% of transformer voltage; response time 0–15 sec to 4 min per 1% deviation; set-point adjustment range 90–115% UN; current-responsive raising of set point 0–16% UN; overvoltage 100–135% UN; undervoltage 50–100% UN; overcurrent 60–120% IN. Voltage drop compensation for active and reactive components shall be provided, together with a manual/auto selector.

#### 1.3.22 Transport

The transformer shall be transported either empty or partly oil-filled, provided with monitored nitrogen gas overpressure via bottles fixed to the tank, with pressure recorded at each intermediate step (factory, port of departure, port of arrival, and site) to avoid moisture ingress. External accessories shall be removed and shipped separately where necessary, moisture-proof packed. Vibration sensors and recording devices shall be installed and shall record vibration from the factory to the site.

#### 1.3.23 Proof of compliance

As proof of compliance the Bidder shall submit with its bid the Schedule of Technical Data duly filled in and outline drawings of the power transformer(s).

# Chapter 06

# 20 kV MV Switchgear

## 1. 20 kV Switchgear

This section of the specification covers the technical requirements for the 20 kV switchgear at the Qush Tepa and Darzaab Substations.

### 1.1 General

The switchgear shall be of metal-clad, compartmented design for indoor installation, of type-tested assembly (TTA) according to the specified IEC standard. Cubicles shall be provided with a single copper busbar system and draw-out type circuit breakers.

All incoming and outgoing feeders shall be equipped with withdrawable vacuum circuit breakers with motor-driven stored-energy mechanisms, having a defined test position in which the breaker contacts on the high-voltage side are isolated.

Permanently installed, short-circuit-proof earthing switches shall be provided in the lower part of the cubicle, mechanically and electrically interlocked with the corresponding circuit breaker. For earthing and short-circuiting the busbars, a conventional earthing truck shall be employed, run in only when the respective circuit breaker is withdrawn; one earthing truck shall be provided for the 20 kV switchgear (earthing by circuit breakers or integrated busbar earthing is also acceptable).

The ambient temperature indoors shall be considered 50°C, appropriate for Jawzjan Province conditions. Condensation shall be prevented by heating controlled by humidity and temperature devices per switchboard. None of the switchgear cubicles may be offset — the operating side must form a straight line. At least 15% of fully installed spare terminal-board capacity shall be available in each cubicle after commissioning.

Installation

All switchgear cubicles shall be mounted on sub-frames provided specifically for this purpose and delivered by the Contractor prior to dispatch of the cubicles. Panels shall be arranged for free installation in the room.

Partition

Individual cubicles shall be compartmented from one another by metal partitions or an approved equivalent system, into: compartments for circuit breakers; busbars; instrument transformers; cable connections; and the relay and control compartment.

IAC classification

The switchgear shall be IAC classified as specified in the Schedule of Technical Data.

### 1.2 Switchgear components

The switchgear and main equipment items shall include, at least: multiple functional compartments separated by partitions and shutters; single busbar system; withdrawable vacuum circuit breakers with motor-driven stored-energy mechanism and automatic shutters over insertion contacts when withdrawn; cable connection compartment with the necessary current and voltage transformers and earthing switch; fuses and voltage transformers for busbar measurement and earth-fault protection; protection relays, coupling relays, mini circuit breakers, terminal boards and meters with LED illumination; a mimic diagram on the front of each cubicle; heating units; an earthing truck or integrated busbar earthing; and fire-proof floor closures for outgoing power cables.

#### 1.2.1 Circuit breakers

The circuit breakers shall be of vacuum type, motor operated and withdrawable.

#### 1.2.2 Earthing switch

The earthing switch shall have the same rating as the main circuit and shall be interlocked with the circuit breaker to avoid switching onto a closed earthing switch.

#### 1.2.3 Current and voltage transformers

The thermal withstand capability of the instrument transformers shall be considered in the design, and all current transformers shall be mounted in the fixed part of the cubicle. Cast-resin insulated, corona-free current transformers shall be used, capable of withstanding dynamic and thermal short-circuit stresses, with separate cores for protection and measurement (intermediate transformers to be avoided). Cast-resin insulated, corona-free voltage transformers shall be used, with three single-phase units in the in-feed cubicles; secondary sides shall generally be safeguarded by MCBs, with separate MCBs per purpose where the same voltage is used for measurement, protection and metering. Metering-core secondary circuits, including cabling to the meter panel, shall be completely sealed.

#### 1.2.4 Interlocking

As a minimum: switching operations shall be performed with the circuit breaker compartment door closed; the compartment door shall be prevented from opening unless the unit is isolated; the feeder earthing device shall not be operable while the circuit breaker is in service position; busbar earthing shall only be possible when all adjacent circuit breakers are in the draw-out position; earthing switches shall not be closed or opened unless the relevant equipment is isolated; mechanical interlock shall permit closing the earth switch only in the test position, and once closed, prevent racking the breaker into service; any interlock defeatable without special tools shall be provided with padlocking; withdrawable units shall be prevented from being withdrawn/replaced without being isolated; and, for incoming feeders, a direct interlock shall prevent closing the sending-end breaker while the earth switch of the incoming feeder breaker is closed, with earth switches closed only when the connection is confirmed dead via voltage-transformer-derived interlocking criteria.

#### 1.2.5 Mimic diagram and local indications

A coloured mimic diagram shall be provided on the front of each cubicle with graphical symbols and indicator lamps, including at least: busbar; circuit breaker position indicator; circuit breaker operating buttons; earthing switch with position indicator; and transformer symbol. Additional indications on the front door shall include: truck in test position; truck in operating position; circuit breaker tripped; no control voltage; no motor voltage; and mini circuit breaker tripped (with separate indication for voltage-transformer protection MCBs). All outgoing feeders shall be equipped with a main metering system and a check metering system in a separate panel.

#### 1.2.6 Control of the switchgear installations

The switchgear shall be controlled from the local control compartment, with each circuit breaker capable of local operation via close/open push-buttons or rotary switches covered in normal operation, and an emergency-open capability if control voltage fails. In the event of a protective trip, means shall be provided to prevent automatic reclosing, overridable only from the switchgear cubicle. Control voltage shall be made available at least twice per switchgear installation, with diode-decoupled and monitored supply, permanently wired panel to panel and safeguarded per panel by MCBs whose tripping is locally indicated. MCBs shall be provided for local controls/interlocks, local annunciation/fault indication, and the power supply to the motor-driven stored-energy mechanism.

#### 1.2.7 Local auxiliary relays and measuring instruments

Fixed-mounted or plug-in type auxiliary relays are applicable; shock-sensitive instruments, relays and meters shall be protected against vibration. Only square instrument shapes shall be used. As a minimum, the following measurements shall be provided locally: triple current indication in all in-feeds; single current indication in phase L2 of all outgoing feeders; single voltage indication (moving-coil type, class 1.5); and a 4-way voltmeter selector for phase-to-neutral and phase-to-phase measurement in all in-feeds.

#### 1.2.8 Cabling and wiring inside the switchgear cubicles

Plug-in connections shall be provided for all auxiliary contacts between the switchgear truck and the fixed part of the cubicle, arranged so trucks are universally interchangeable without altering the wiring. No cable openings shall remain open after commissioning; the Contractor shall fit pressure-tight screw plugs where cables are absent. A sufficient number of round-ended earthing studs shall be provided on the collector bars. All secondary equipment shall be wired to terminal strips, and instrument transformer secondary circuits shall be wired individually with short-circuit links on current transformer terminals. Colors and minimum wiring cross-sections shall be per Appendix-1, General Technical Requirements.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

Catalogs and the operation manual for the switchgear shall be supplied, together with the number of switchgear units produced in the last 5 years and a consumer list, and requirements per IEC 62271-200 Clause 9.102.

# Chapter 07

# MV and Low Voltage Cables

## 1. MV and LV Cables and Cable Support Structures

### 1.1 General

This section covers the technical requirements of the medium voltage and low voltage cables within the Qush Tepa and Darzaab Substations, including cable sealing ends, cable joints, trays, risers, supports, structures and all associated equipment, complete in every respect and suitable for satisfactory operation.

### 1.2 Technical requirements

#### 1.2.1 General

The requirements specified under General Technical Requirements Section B0.2 shall also apply, together with further regulations of the other sections of this Specification. Individual cable lengths shall be laid in one piece. All cables laid on the surface of walls, steel frames, etc. shall be protected against mechanical damage by galvanized steel tubes or robust PVC pipes; in walk-way areas, only steel tubes shall be installed.

For running out power cables, heavy screw jacks and spindles shall be used, with the cable continuously pulled from the upper side of the drum over rollers placed at intervals of 4 m max. Sharp edges in trenches or duct ends shall be covered to prevent cable damage. Cables installed above ground and exposed to direct sunlight shall be protected by sunshields, given the high solar exposure typical of Jawzjan Province.

During the approval procedure, the Contractor shall provide a cable schedule listing all cables and their destination, including number of cores, core size, cores in use and spare cores, and cable length, for each substation.

#### 1.2.6 MV cables

This section contains the specific requirements for the design, ampacity, raw material, components and production of XLPE-insulated cables for a rated system voltage of up to 30 kV and their accessories, suitable for the 20 kV auxiliary and distribution supply of the specified substations.

#### 1.2.6.1 Cable design

The single-core MV cable shall contain a stranded and compacted Class 2 copper conductor per IEC 60228. The semi-conductive conductor screen, XLPE insulation and semi-conductive insulation screen shall be extruded simultaneously in a dry-curing process, with the outer semi-conductive layer bonded to the insulation and peel-able. Special care shall be taken to prevent galvanic corrosion, with water sealing remaining effective even where a damaged section is replaced by jointing a new length.

A cable screen of bare copper wires and copper tapes (counter helix), an overlapped swelling tape separator and a black overall PE sheath shall be applied. The PE sheath shall be medium-density polyethylene (MDPE) with minimum tensile strength 18 N/mm² and minimum elongation at break 300% per IEC 60811-1-1, suitable for a minimum installation temperature of −10°C. Cables shall be capable of continuous operation at 90°C and manufactured for direct burial as well as indoor/outdoor and duct installation. The outer sheath shall be marked with length every 1 m and cross-section; each phase shall carry a continuous colored stripe (red, yellow or blue).

#### 1.2.6.2 MV Cable accessories

Cable terminations

Terminations shall be one-piece, sheds-free, heat-shrinkable, with a stress-control layer and a co-extruded double-layer insulation tube free of air gaps before and after installation, non-tracking, erosion and UV resistant. Active, complete sealing shall be provided at both ends of the termination via hot-melt or sealing mastic. Cable lugs shall be screw bimetallic (Al-Cu) construction with shear-off head bolts, included in the kit.

Cable joints

No cable joints shall be used.

Cable markings

Packing shall protect goods against water ingress and mechanical damage; components shall be storable without deterioration over −5°C to 40°C with no shelf-life limitation. Each kit shall include English-language installation instructions and a printed label stating batch number, applicable cable cross-section range, joint part description and manufacturer's name.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

A calculation report of the cable cross-section shall be submitted with the bid.

#### 1.2.10 Low voltage cables

Low voltage power and control cables shall comply with the specified IEC requirements. For the 400/230 V level, single, two, three and four-core low voltage power cables shall be used with a minimum cross-section of 2.5 mm², PVC insulated and sheathed, suitable for continuous operation at 70°C max., each core with a solid round copper conductor with colored insulation. DC cables shall consist of single, two or four-core cables, generally single-core for battery/rectifier to DC switchgear connections. Low voltage and DC cables shall be rated E/E0 0.6/1 kV. The star point of the 400/230 V system shall be solidly earthed, with cable screens connected to the neutral as a protective measure against excessive contact voltage (protective multiple earthing).

Instrument transformer cable

Each voltage transformer circuit shall be wired via a separate MCB to the switchgear control cubicle. Instrument transformer cables shall be designed for E/E0 = 0.6/1.0 kV, minimum cross-section 2.5 mm² inside buildings and 4 mm² outside, checked by the Contractor and increased where necessary.

Metering cables

The minimum cross-section shall be 6 mm², and the cables shall be laid completely sealed.

Cables for control, measuring and signaling

All such cables shall be of stranded-conductor type; the number of cores in multi-core cables shall be selected from 2, 3, 4, 7, 12, 19, 27 and 37, with 10% spare capacity per cable type. The Contractor shall terminate all power and control cables inside the switchgear cubicle. Minimum cross-sections and wiring colors shall be per Appendix-1, General Technical Requirements. All cabling and wiring must be accessible from the front of panels/cubicles.

Cables for lighting

Lighting cables shall comply with the specified IEC and rated voltage, standard multi-core with copper conductors and non-hygroscopic filler. The PVC over-sheath shall be oil-resistant and fire-retardant, colored black for external and white for internal lighting.

Heat resistant cables

Cables used where ambient temperature exceeds 60°C shall be heat resistant, suitable for continuous operation at 180°C ambient, with Teflon or silicone insulation.

#### 1.2.11 Cable connections and sealing ends

All cables shall be prepared and connected to terminal strips, terminal screws and apparatus terminals as required, and fixed to appropriate supporting structures. Cable sealing ends shall be provided for all cables supplied under the contract. Minimum bending radius, maximum tensile stress and cable spacing shall be observed. A minimum creepage distance of 3.1 kV/cm shall be considered for cable sealing ends, based on system maximum voltage phase-to-earth. Straight-through joints, where unavoidable, shall be of the heat-shrinkable type; terminations and sleeves shall be of flame-resistant synthetic material with reduced-flammability additives. Cables shall be fixed at the sealing ends to cable supports using corrosion-resistant clamps.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

Supports for cable terminations and cable trays

Cable terminations shall be placed on suitable, rigid steel support constructions designed to withstand all static and dynamic forces under all operating conditions, with at least one anchoring clamp below each termination. Requirements for cable trays specified in Section B0.2 shall be observed. Separate cable trays and risers shall be provided for: power cables above 1,000 V; power cables below 1,000 V; DC power cables; instrument transfer cables; and control/measuring/signaling cables above 60 V. All T-junctions, cross-overs and bends shall use prefabricated tray elements to avoid cable crushing at transition points, with adequate spacing to prevent mutual interference. Cable tray material shall be hot-dip galvanized, minimum thickness 100 micrometers.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

# Chapter 08

# AC and DC Installations

## 1. AC DC Supply and Installations

### 1.1 General

This specification covers the design, manufacture, acceptance testing in the Contractor's workshops as well as the supply, delivery, unloading, erection, commissioning, marking and trial operation of the AC and DC installations for the Qush Tepa 220/20 kV Substation and Darzaab 220/20 kV Substation, complete in every respect and suitable for satisfactory operation.

### 1.2 Technical Requirements

#### 1.2.1 0.4 kV switchgear

The 0.4 kV switchgear shall comply with IEC 61439-1 and -2 (latest version), designed and manufactured as a test-verified assembly, provided in metal-clad, compartmented design with fix-mounted units for indoor installation. The necessary instruments, control switches and switch drives shall be fitted on the front panel of each switch unit. The 0.4 kV distribution shall be fed from the LV system of the auxiliary supply. The complete installation shall be designed for continuous operation at 50°C ambient temperature, appropriate for Jawzjan Province, and the Contractor shall ensure a minimum of 5% fully equipped reserve capacity is available after hand-over.

#### 1.2.2 Switchgear minimum requirements

As a minimum, the switchgear shall consist of: metal-clad, partitioned switchgear cabinets; a single busbar system with the necessary current transformers; busbar earthing pins with earthing fittings; compartments for busbars, breaking units and cable connections, each separately partitioned; fire bulkheads below switchgear cabinets; numerical protection relays with the incoming circuit breaker for monitoring, position indicators, warning and control devices, a mimic diagram and complete terminal strips; MCBs with auxiliary contacts for signaling of failure to different consumers; a temperature- and humidity-controlled heating system for each cabinet; and all CBs, isolators and MCBs equipped with minimum spare auxiliary contacts (2 'on' and 2 'off').

#### 1.2.3 Basic equipment

The 0.4 kV switchgear shall incorporate: a circuit breaker unit for the infeed; the necessary outgoing MCBs, thermal trips, control voltage, instrument transformers and measuring instruments; the necessary current transformers; a relay recess with protection/monitoring relays and terminal strips; a partitioned cable connection cabinet with protected cable fittings; one 230 V/10 A single-phase convenience outlet; and ventilation slots.

#### 1.2.4 Mimic diagram

The mimic diagram shall, as a minimum, contain the auxiliary transformer symbol, the 0.4 kV circuit breaker position indicator with actuating components, and the 0.4 kV busbar. All circuit breakers shall be designed for local control with the necessary control and position-indicating contacts. The switchgear cabinet shall be installed rear-side to the wall with a sufficiently large front gangway.

#### 1.2.5 Current transformers

Accuracy for measurement shall be class 1.5 M5, and for protection class 10P10. Transformers with cast-resin insulation shall be used, withstanding dynamic and thermal short-circuit stresses, with intermediate transformers avoided. Separate cores shall be provided for protection and measurement, with three single-phase current transformers in the infeed.

#### 1.2.6 Terminals and cabling

Connection terminals shall be suitable for cable cross-sections of 4 mm² for motors/consumers up to 5.5 kW and 10 mm² for 7.5–11.0 kW. Plug connections shall be provided for all auxiliary contacts, allocated so circuit breakers are universally interchangeable without altering the wiring. As a minimum, cable connections shall be possible for control/annunciation circuits (2.5 mm²) and instrument transformer circuits (4 × 4 mm²). Individual instrument transformer secondary circuits shall be wired to the circuit breaker cubicle terminal strip, with short-circuit bridges on current transformer terminals. Separate MCBs with auxiliary contacts shall be provided where voltage is used for various purposes, with MCB tripping indicated in the control room by a group signal.

#### 1.2.7 Auxiliary relays and measuring instruments

Only square-shape measuring instruments shall be used. All incoming feeders with circuit breakers shall be equipped with a triple moving-iron ammeter and a single voltmeter with a four-way change-over switch for phase-to-phase and phase-to-neutral measurement.

#### 1.2.8 Control

Circuit breaker operation shall be by commands given at the front panel of the distributor via 'on-off' buttons covered in normal operation.

#### 1.2.9 Signaling

All signaling, monitoring and other contacts shall be wired to the associated terminal strip and processed in the control system used. Each 0.4 kV circuit breaker shall be equipped with indicator lamps/position indicators showing: 'off'-open position; 'off'-due to fault; and 'on'-operating position, indicated on the cubicle and in the control system. A summary alarm shall be shown for MCB tripping.

#### 1.2.10 Installation

All switchgear cabinets shall be installed on base frames provided specifically for this purpose, supplied by the manufacturer of the 0.4 kV switchgear.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

Instruction manuals for the distribution facility shall be supplied with the bid.

#### 1.2.14 DC installations

#### 1.2.15 DC distribution cubicles

The DC distribution cubicles shall comply with IEC 61439-1/2 (latest version), designed and manufactured as test-verified assemblies. The DC distribution cubicle and battery chargers shall be installed in metal-clad, partitioned cabinets with fixed equipment and a single busbar system, in the substation control building, with terminal strips and cable-end attachment components arranged in the lower part of the cabinet.

The main distribution cubicle shall be fed by a lead-acid battery (100%) and one charger (1 × 100%), connected in parallel to the consumers. The infeed switch shall be a manually operated circuit breaker; output switches shall be MCBs; the busbar shall be fitted with a voltmeter. Manual load switches, fuses, contactors, shunts and measuring instruments shall be neatly arranged in the appropriate compartments, with single-phase cable connections from the charger and batteries.

The complete installation shall be designed considering local ambient conditions, with suitable heaters in the switch cabinets to prevent condensation. The Contractor shall ensure a minimum of 5% fully equipped reserve capacity and 15% spare terminal-strip capacity after hand-over. As the 220 V DC system is an insulated network, it shall be equipped with an insulation control device installed in the main distribution board.

Technical data

The required technical data are specified in the Schedule of Technical Data, Appendix-1.

Test requirements

Test requirements as specified in the Schedule of Technical Data shall be followed. A type test report shall be accepted where the type tests have been performed within the last 5 years by an independent, internationally accredited testing institute.

Proof of compliance

As proof of compliance the Bidder shall submit with its bid:

- The technical data sheets duly filled in.

- Confirmation of the test requirements as included in the Schedule of Technical Data.

- Proof of experience in manufacturing, including the number of units produced and a list of projects in which they have been used.

Instruction manuals for the distribution facility shall be supplied with the bid.

#### 1.2.19 220 V and 48 V battery charging equipment

Battery chargers shall comply with IEC 60146, suitable for charging and floating the battery while simultaneously supplying the DC consumers, provided as thermistor-controlled devices with current-voltage characteristics for standby parallel operation.

Digitally controlled and monitored equipment shall be provided, comprising: radio interference suppression per the applicable IEC regulations; monitoring of the charging circuit for charging and interruption; and voltage monitoring of the incoming three-phase supply, with automatic disconnection at +15% over-voltage and −15% under-voltage (without periodic interruption from voltage surges), with a fault alarm on the front door at −15% under-voltage. All disconnection events shall be indicated as a fault alarm and combined into a collective 'rectifier fault' signal wired to the terminal strip and control room.

The chargers shall be equipped with automatic boost-charge stages settable at 1.75 V/cell between 1 and 8 hours after input failure, and filter units with ripple content below 2%. The Contractor shall provide all necessary monitoring equipment, measuring instruments, switches, indicator lamps and cable fixings on the front of the rectifier cubicles.

#### 1.2.20 Technical data

The technical data shall be as specified in the Schedule of Technical Data, Appendix-1.

#### 1.2.21 Test requirements

Test requirements shall be indicated by the Bidder.

#### 1.2.22 Proof of compliance

The Bidder shall submit with its bid the schedule of technical data duly filled in, and instruction manuals for the battery charging equipment.

#### 1.2.23 220 V and 48 V batteries

Batteries shall comply with IEC 60086-1; lead-acid type batteries shall be provided for the DC system. Batteries shall be mounted on insulated wooden or metal frames with consoles, with all necessary interconnection and fixing material. Battery capacity shall be matched to the requirements of the control and protection circuits, and justified by the Contractor considering a discharge time of 10 hours and the connected load. A complete set of test and maintenance accessories, including a syringe hydrometer and a durable instruction card, shall be provided for each battery. Battery cases shall be of high-impact polystyrene translucent plastic, with cells numbered consecutively and terminal cells marked to indicate polarity.

#### 1.2.24 Technical data

The technical data specified in the Schedule of Technical Data shall be observed.

#### 1.2.25 Test requirements

Test requirements shall be indicated by the Bidder.

#### 1.2.26 Proof of compliance

The Bidder shall submit, as proof of compliance: the schedule of technical data duly filled in; catalogs of the equipment proposed; and a single-line diagram showing the proposed DC system.

# Chapter 09

# Lighting and Small Power Installation

# Qush Tepa 220/20 kV Substation and Darzaab 220/20 kV Substation

## 1. Lighting and Small Power Installation

### 1.1 General

This specification covers the design, manufacture, pre-assembly and acceptance testing in the Contractor's workshops as well as the supply, delivery, unloading, erection, adjusting, identification, commissioning and trial run of the lighting system and small power installations for the Qush Tepa 220/20 kV Substation and Darzaab 220/20 kV Substation, complete in every respect and suitable for satisfactory operation.

### 1.2 Technical Requirements

#### 1.2.1 Lighting Installation

#### 1.2.2 General

The requirements specified in Appendix-1 General Technical Requirements shall be observed as well as the requirements below.

All lighting fittings and all equipment comprising the lighting sub-distribution units must meet the operating requirements in full at the specified ambient conditions. The lighting fittings shall be designed for the specified operating voltage. For protection against contact with live components, all lighting fixtures must be suitable for the following protection measures:

- protective conductor connection, or protective insulation;

and must visibly carry the accepted symbol to indicate this.

In plant areas subject to danger of explosion (i.e. battery rooms, if applicable) the necessary explosion-proof lighting fittings, cable connection boxes and pushbuttons are to be used according to IEC 60079. Sub-distribution units shall not be installed in such rooms or areas.

#### 1.2.3 Sub-distribution Boards

Metal-clad sub-distribution boards (protective type IP 54) suitable for flush or surface mounting on the walls shall be provided. Each sub-distribution board must at least be equipped with:

- manual feed-in change-over switches with I - 0 - II positions;

- one voltmeter with voltmeter switch for measurements between the individual phases and the neutral as well as between two phases; 5 bus bars for 3-phase system, neutral and earth;

- the necessary single-pole MCBs for lighting circuits and control;

- the necessary single-pole MCBs for domestic power outlets (sockets);

- the necessary single-pole MCBs for power sockets;

- the necessary current relays and contactors for push-button energizing, de-energizing of lighting circuits.

The sub-distribution boards are to be designed so that after handing over, 15% reserve feeders are still available.

#### 1.2.4 Internal Lighting

Generally, lighting fixtures wired for three-phase supply and fitted with new and well-branded LED lamps are to be provided for the control building.

The lighting fixtures are to be selected so that they can be used for single or strip lighting.

The room lights shall generally be controlled by pushbuttons via current impulse relays. The pushbuttons must be located at the access doors to the appropriate rooms.

The internal lighting must be designed to give the lighting intensities according to the relevant standards and the use of different rooms. An ageing factor of 20% must be taken into account, and therefore the lighting intensities of the fittings when new (new value) must be achieved as a minimum during the Tests on Completion.

| Location, Room | Type of Lighting Fixture | Lighting Utility Value (Lux) | Density New Value (Lux) |
| --- | --- | --- | --- |
| Control room | 3 | 550 | 600 |
| Relay room | 2, 4 | 300 | 360 |
| Battery room | 2 | 200 | 240 |
| Toilets and store | 1 or 2 | 100 | 120 |
| Corridor, passage ways | 3 | 100 | 120 |
| Machine room | 2, 4 | 100 | 120 |
| Workshop room | 3 | 200 | 240 |

Throughout the rooms and grounds, the lighting density must be 200 Lux on local measuring and control stands and instrument panels.

Key to light type numbers of the above table:

- 1. Free-beaming LED lighting luminaries, protection degree IP 32;

- 2. Watertight LED lighting luminaries, protection IP 64;

- 3. LED lighting luminaries with protective cover, protection IP 32;

- 4. LED lighting luminaries, protection IP 54.

The LED lighting fitting should be equipped with integrated LED modules of 1 x 58 W or 2 x 58 W. Where required, LED lighting fittings equipped with high-power LED lamps equivalent to 1 x 250 W or 1 x 400 W halogen output shall be used for high-bay/outdoor applications.

The color of the light produced by the lamps must be selected according to requirements. If different lamps are used in the same room, then lamps giving the same color of light are to be used in accordance with the requirements.

Internal lights must be connected in 3-phase circuits so that only every third lamp will fail in the event of failure of a single phase. Cables with a cross-section of at least 2.5 mm² are to be used as lighting cables for LED lights.

#### 1.2.5 Emergency Lighting

The emergency lighting shall be operated from the 220 V DC system. In the event of a black-out the emergency system shall be operated automatically. A manual change-over facility shall also be provided.

The emergency lighting shall be designed simply as emergency escape route lighting. At least one emergency light must be visible from every point in the room. The lighting intensity must be at least 50 Lux.

#### 1.2.6 Outdoor Lighting Including Security Lighting

The switchyard lighting system shall be an outdoor lighting system, applicable to both the Qush Tepa 220/20 kV switchyard and the Darzaab 220/20 kV switchyard. The lighting utility value shall be 14 Lux. In addition, a security lighting system along the substation fence shall be installed at each substation.

#### 1.2.7 Technical Data

The required technical data are specified in the schedule of technical data.

#### 1.2.8 Test Requirements

Test requirements are specified as per compliance to Technical Data Sheets.

#### 1.2.9 Proof of Compliance

As proof of compliance the Bidder shall submit with its Bid:

- the Schedule of technical data duly filled in;

- catalogs with the material to be supplied, to be included in the Bid.

#### 1.2.10 Power and Protection Sockets

#### 1.2.11 General

The power and protective sockets are intended for the plug-in connection of mobile electrical equipment for repairs and maintenance of any kind. The mobile electrical equipment must be fitted with the necessary 3-phase and earthing contact plugs.

#### 1.2.12 Power Sockets

The power supply to the power sockets shall be provided from sub-distribution boards to be installed. In each substation building and in the 220 kV switchyard nearby the power transformer, at least 1 power socket system shall be installed. Plugs and sockets must be in accordance with CEE form. Generally, different power sockets are to be used, with stainless steel metal casings resistant to impact, direct sun etc. and suitable for service wall mounting. The sockets are to have a degree of protection of at least IP 54. All the sockets shall be of outdoor type, even if installed indoors, and shall operate satisfactorily under direct sunlight.

Each socket system shall be equipped as follows as a minimum requirement:

- with the necessary wire inlets at the top of the power socket casing for the incoming and the outgoing feeders including the necessary glands or blanking plugs;

- with the necessary fuses in the top of the metal casings;

- with the necessary main manual switch before the fuses of the socket circuits in the top of the metal casing;

- with a three-phase socket 400 V, 32 A, 5-pole (three-phase, neutral and earth) in CEE form (CEE = International Commission on Rules for the Approval of Electrical Equipment) in the bottom of the metal casing;

- with two AC single-phase sockets 230 V, each 16 A, screwed, 3-pole (phase, neutral and earth) in CEE form, in the bottom of the metal casing;

- with all the necessary fuse bases, connection and its intermediate terminals and any other attachment fittings.

All sockets shall be provided with plugs. The power supply of the sockets shall be generally provided with PVC power cables. For the internal wiring in the metal casing, stranded copper conductors with PVC insulation shall be used.

#### 1.2.13 Domestic Power Outlets (Sockets)

In rooms such as switchgear, relay room, battery, control, office etc. the domestic power outlets (sockets) are to be provided in adequate quantity in accordance with the requirements, surface-mounted. All sockets shall be provided with plugs. The power supply shall be provided from the lighting distribution boards. The power outlets must be 16 A, 3-pole type, i.e. phase, neutral and earth.

All sockets must be in accordance with CEE form. In the corridors, one power outlet must be arranged every 10 m.

Generally, plastic-insulated power outlets for 230 V AC are to be provided. The power outlets (sockets) shall be fed via the single-pole MCBs of the lighting distribution units via three-core cables. Not more than five power outlets (sockets) may be fed from one circuit. The conductor cross-section must be at least 4 mm² for the cables supplying the sockets.

#### 1.2.14 Technical Data

The required technical data are specified in Technical Data Sheets (Appendix-1).

#### 1.2.15 Test Requirements

The required test requirements are specified as per compliance to Technical Data Sheets (Appendix-1).

#### 1.2.16 Proof of Compliance

The following information shall be provided as proof of compliance:

- the Schedule of technical data shall be duly filled in;

- catalogs of the proposed materials to be included in the Bid.

# Chapter 10

# Earthing System and Lightning Protection

# Qush Tepa 220/20 kV Substation and Darzaab 220/20 kV Substation

## 1. Earthing System and Lightning Protection

### 1.1 General

This specification covers the design, manufacture, pre-assembly and acceptance testing in the Contractor's workshops as well as the supply, delivery, unloading, erection, adjusting, identification, commissioning and trial run of the earthing and lightning protection system for the Qush Tepa 220/20 kV Substation and Darzaab 220/20 kV Substation, complete in every respect and suitable for satisfactory operation.

### 1.2 Technical Requirements

#### 1.2.1 Earthing and Lightning Protection

#### 1.2.2 General

The requirements specified in Appendix-1 General Technical Requirements shall be observed as well as the requirements below. For the 220 kV outdoor installations at both the Qush Tepa and Darzaab substations, a meshed earthing system shall be installed. The lightning protection system shall comply with the specified IEC.

The earthing system shall be calculated according to IEEE 80, considering actual soil conditions and the specified short-time currents at each substation site. For the construction of the earthing system, approved standards such as VDE 0141 or similar standards shall apply also.

A uniform stranded conductor cross-section is to be used for the entire installation. For potential grading and to offer protection against excessive contact potentials, ring earths made of stranded copper cable shall be installed around the building and these shall be connected to the mesh earth conductors.

At maximum distances of 10 m, the ends of the stranded conductors of the mesh earth (earthing electrode) shall be connected to the internal main earthing ring.

The earthing and lightning protection system shall include, but not be confined to:

- the necessary stranded copper earthing conductors for the indoor earthing installations and mesh system (earthing electrode); the necessary stranded copper conductor for the earthing ring inside the building;

- connection of PVC single-core cables being laid out of the concrete to the earthing ring inside the buildings;

- the necessary compression connectors or connections by thermo-weld system (or similar) for the earthing electrode conductor crossing point connections and junctions;

- all connections to the housings of the electrical apparatus, steel frames, pipes, steel strips etc.;

- all necessary disconnecting points for measuring purposes, which must be readily accessible;

- all the necessary lightning protection equipment for the protection of persons and structures such as lightning overhead wires, roof bushings, lightning rods, potential equalizing systems, spark gaps, lightning arresters etc.; the required connecting and fixing material such as plugs, screws, angle pieces, expansion strips, conductor support, isolating terminals, earthing and rain gutter clamps, jumper outfits, earthing clamps etc.

#### 1.2.3 Material

Whenever dissimilar materials are to be joined, the necessary transition plates are to be inserted as required to make sure that electrolytic action is avoided.

Earthing material

Stranded copper conductor is to be used as earth conductor for laying on cable trays and for the earthing of electric equipment, steel structures and frames etc. The same material shall be used for the internal earthing rings inside the buildings and also for the underground earthing electrode.

Lightning protection material

Round hot-dip galvanized steel rod of 50 mm² is generally to be used as the material for the lightning protection system rods. The conductor supports of the lightning protection system must be earthed. Nuts and bolts at isolating or other points, which are to remain detachable, must be made of hot-dip galvanized material. The overhead wire shall be of stranded hot-dip galvanized steel conductor.

#### 1.2.4 Earthing System

Installations above and below 1000 V shall be made safe by protective earthing. This is required to prevent the occurrence of excessive touch potentials on conducting parts of the installation, which are not part of the electrical circuit.

The earthing installations must be designed and constructed in accordance with approved standards.

Generally, in the whole substation area and underneath the substation buildings of each substation, a grid earth of stranded copper cable must be installed. The size of the stranded copper conductor shall be minimum 120 mm², but the Contractor has to check this cross-section by an earth fault calculation for each site. The size of the mesh shall be in accordance with the maximum occurring earth leakage current to meet the requirements for earthing according to IEEE 80.

The size of the stranded copper conductors used must be uniform throughout the area under Contract as far as possible. From the inner earthing ring, the connections to the switchgear and other electrical apparatus, cable trays, vertical cable runs, steelworks etc. are to be made using stranded copper conductor. All the electrical equipment, frames and mechanical apparatus must be fitted with earthing screws and studs.

The copper conductors can be laid and fixed on the cable trays and vertical runs for AC power cables. Where this is not possible, earthing conductor supports shall be provided and fixed in concrete or masonry by means of plugs. The bare copper stranded conductor must be fixed with earthing support on walls.

Cable trays and vertical runs shall be connected to the earthing conductor at intervals of 10 m max. in such a way as to give good connection. This earthing conductor must likewise be connected to the earthing ring.

Inside the concrete of buildings, a separate round iron (reinforcement bar) mesh in walls and ceilings for earthing purposes must be provided. The size of this mesh should not exceed 8 m x 4 m. The connections of this earthing reinforcement bar should be welded. The reinforcement bars shall be connected via a flexible PVC single-core cable every 8 m to the inside earthing ring.

The inside earthing ring of the buildings must be connected with the outdoor earthing system. These connections must be provided with flexible PVC single-core cables, which are to be laid through the concrete walls above the ground water level.

The crossing point connections of the earthing cables underneath the buildings and outside the buildings must be made by compression connectors. Connections, e.g. by thermo-weld system, will also be acceptable. All other earthing conductor connections and junctions must be made in the same way to ensure secure, lasting connections having good contact.

The interconnections between the earthing installations of the buildings must be provided with an accessible isolating point in order to be able to measure the earthing resistance. All isolating points must be numbered consecutively in the drawings and clearly marked in the field.

All facilities shall be securely connected, with minimum practicable resistance, to the common ground system. The maximum resistance to ground from the connection point in any facility shall not exceed 0.5 Ω when measured by standard ground resistance measurement techniques in dry season.

The lightning installations must also be connected to the central earthing installation.

The effects of lightning strikes on the control and monitoring systems vary from faulty pulses in control and measurement to the destruction of electronic sub-assemblies and cables and must therefore be prevented by the earthing of screens. To this end the screens of the control cables leading from the signal transmitters, actuators etc. must be taken to the central earthing points and from there to the indoor earthing installation.

They must be insulated and laid via the screen bars in subsidiary distribution boxes, intermediate terminal boxes, marshalling racks, control cabinets and DC main distribution boards.

#### 1.2.5 Technical Data

The required technical data for the earthing system are specified in the schedules of technical data.

#### 1.2.6 Test Requirements

The test requirements are specified as per compliance with Technical Data Sheets.

#### 1.2.7 Proof of Compliance

As proof of compliance the Bidder shall submit with its Bid the schedules of technical data and test requirements duly filled in. The Bidder shall also submit a brief description of the intended system to be provided at each substation.

#### 1.2.8 Lightning Protection System

The planning, dimensioning and construction of the lightning protection system shall be according to the specified standard.

The rolling sphere principle shall be applied for the design of the system. All outdoor equipment shall be protected against lightning strikes by means of lightning collectors and conductors.

The collectors shall be arranged in such a way that, as far as possible, they collect all lightning strokes without these directly striking the parts to be protected.

The buildings shall be protected against lightning strikes by means of lightning collectors and conductors. The collectors are to be arranged in such a way that, as far as possible, they collect all lightning strokes without these directly striking the parts to be protected. This condition is considered to have been fulfilled if no point on the roof surface is more than 8 m away from a collector. Collector lines suffice as collectors, e.g. along the ridge, at gables and eaves.

Ridge conductors must be taken right to the end of the ridge. Moreover, roof conductors should run as natural continuations of all main conductors.

Conductors at the gable extremities or eaves must be laid in the closest possible proximity thereto. In the case of steel-framed structures, the ridge conductors must be connected to the roof supporting structure at least every 8 m. Lower-level annexes are also to be provided with collectors. Roof lines and other conductors are to be laid and fixed in such a way that they can withstand the stresses expected from storms, lightning strokes, roof work etc.

One main conductor between the lightning collectors mounted on top of the building and the potential grading ring laid in the ground are to be provided every 8 m of the aforementioned lightning collector. The maximum spacing between conductor fixings may not exceed 1.25 m for horizontal runs and 1.25 m for vertical runs.

All main and secondary conductors, which are connected to an earthing conductor, must be provided with an accessible isolating point in order to be able to measure the earth resistance. All isolating points must be numbered consecutively in the drawings and shall be labeled at the buildings and at the switchyard steel structures.

Nuts and bolts at isolating or other points, which shall remain detachable, must be made of copper-nickel-silicon-bronze.

All main and secondary conductors are to be connected, using compression connectors, to the earthing ring running around the buildings and tanks at a distance of 1 m and a depth of 0.8 m. At the connection points, the copper conductor and the round copper rod must be stripped of the lead sheath. The subsoil connection points are to be protected against corrosion by wrappings or bitumen.

#### 1.2.9 Technical Data

The technical data are specified in the Schedule of technical data.

#### 1.2.10 Test Requirements

The test requirements are specified as per compliance to Technical Specifications.

#### 1.2.11 Proof of Compliance

As proof of compliance the Bidder shall submit with its Bid the schedule of technical data duly filled in as well as the schedule of test requirements. The Bidder shall also submit a description of the lightning protection system it intends to install.

# Chapter 11

# 220 kV and 20 kV Protection including Test Requirements for Qush Tepa and Darzaab Substations

# Qush Tepa 220/20 kV Substation and Darzaab 220/20 kV Substation

## 1. Current and Voltage Transformer Requirements

Current transformers shall have 5 secondary windings and shall be supplied in tropical export version. The rated burden of the protection cores indicated in the data sheets shall be considered as the minimum requirements for all possible ratios; the Contractor may select either primary reconnection or secondary taps in achieving the specified ratios.

The Contractor is responsible for defining the final characteristics of the CT and VT cores for protective relaying functions (dedicated or combined measuring/protection) so as to satisfy the performance requirements of the offered relays. The compliance of the CTs and VTs shall be documented and submitted for Employer's approval prior to manufacturing.

Current transformers shall be preferably of the low reactance type (for all secondary taps in case of multiple ratios). The performance shall not be inferior to that defined in the IEC Publications.

For the class “x” type, the knee-point voltage (defined as the point on the excitation curve at which a 10% increase in the r.m.s. value of the applied voltage results in a 50% increase in the r.m.s. value of the secondary exciting current) shall be, for each of the possible ratios, above the secondary voltage for maximum short-circuit conditions, actual secondary winding resistance at 75°C and 150% of the anticipated external burden.

The following minimum requirements apply:

- magnetizing current at knee-point voltage not higher than 5% of the nominal secondary rated current;

- maximum secondary resistance so as to not exceed 50% of the secondary rated burden.

For the high impedance protection, scheme-specific requirements shall be taken into consideration for selecting knee-point voltage and magnetizing current.

Means for checking the integrity of CT and VT circuits shall be provided, either automatically or manually. The integrity check must be capable of being performed on-line without inhibiting or jeopardizing the protection function. The Bidder shall explain his method of performing these checks.

For ease of commissioning, the CT and VT terminals of the relay panels shall be equipped with links for interrupting or shorting as well as measuring points. Each current transformer circuit shall be earthed through a link at one point only. By interrupting any current transformer circuit at the place before the earthing point (e.g. at the measuring point), it shall be foreseen that the remaining circuit is automatically shorted and this circuit is earthed at another point.

## 2. Auto-reclosing Concept in the Qush Tepa and Darzaab Substations

All protection for 220 kV OHLs described in these clauses shall be designed for operation in conjunction with one three-phase auto-reclosing cycle. Additionally, all protection for the 220 kV OHLs shall be designed for operation in conjunction with one one-phase auto-reclosing cycle plus one three-phase auto-reclosing cycle after an unsuccessful one-phase auto-reclosing cycle.

## 3. References

The protection equipment supplied under this contract and the associated software shall have a demonstrated reliability of at least two years of operational experience in HV substations. The Contractor shall quantify the number of installations for the protection equipment and software which have been undertaken at similar voltage levels and environmental conditions over the last two years.

## 4. Housing, Wiring, Identification

The protection equipment shall be grouped in the necessary number of fully wired, floor-mounted, steel sheet cubicle type panels. Where cubicles are installed internal to buildings, the cubicles shall meet the requirements of IEC Publication 60529, classification IP 52. Any cubicles installed external to buildings shall be IP 54.

The Contractor shall ensure that adequate cooling of the cubicles is provided for external cubicles to compensate for the very high temperatures in summer. Temperature within the cubicles shall stay ≤ 40°C where electronic modules are installed, unless the equipment specification is such that the device proposed can cope with the high temperatures anticipated at the Qush Tepa and Darzaab sites.

Each protection cubicle shall be dedicated to one single protected element. The sequence of the cubicles shall be defined in the Detailed Design. Cubicles shall be fitted with window-type (flame-retarding) protective full doors.

Where protection cubicles are installed in air-conditioned relay rooms of control buildings, the protection cubicles shall be of the self-ventilated type and shall comply with all construction requirements of the above-mentioned sub-section of the Specification. The Contractor shall ensure that in the event of failure of the air-conditioning system, the protective relaying systems, and their associated signaling, monitoring, control and alarm equipment, must remain in full operating condition for a minimum of 24 hours, taking cognizance of the outside ambient temperature and the maximum humidity possible for this region.

Each cubicle shall be provided with an anti-condensation heater with an internal thermostat/humidity sensor to prevent the formation of condensation within the cubicle.

The internal wiring of each cabinet shall be carried out according to the provisions of the General Technical Requirements. Within each cubicle, the wiring associated with each functional assembly shall be segregated as far as possible.

The final paint finish shall comply with the requirements of Appendix-1 or appropriate IEC standard; the color shall be subject to Employer's approval.

Equipment identification shall include:

- feeder (bay) labels;

- individual relay identification (device, ANSI designation numbers and functions);

- terminal identification of external relay connections to CTs, VTs, DC and AC alarms, trips and communication equipment control cable labels.

All internal wiring shall be identified by the use of ferrules at each point of connection.

## 5. Testing Facilities, Indications

Individual relays and protection assemblies intended for panel or rack mounting shall be designed so that the internal functional modules are capable of being extracted from their case or rack without altering any external wired connections (including CT circuits).

Except as stated otherwise, no provision for automatic test facilities is required. Each protection functional assembly shall be provided with easily accessible field-testing terminal blocks/sockets. Where Main and Backup or duplicated protection systems are provided, testing of one protection system shall be possible without degrading the function of the other.

The protection schemes shall be provided with local and remote DC supply supervision and with the following minimum local indications, manually or electrically resettable, allowing for a reliable and precise post-fault/test response analysis:

- faulty phase (where applicable) or general starting operating time or time zone;

- tripping, receiving and sending of all associated HF signals (manipulated/blocking/permissive/direct trip);

- associated PLC channel(s) failure;

- test/in/off status (in conjunction with a lockable switch with remote position indication).

The operating indications shall not be lost in case of auxiliary supply interruption. Means for testing of the indicators shall be provided at relay case or panel level.

The indications shall be clearly visible without opening of relay cases or relay cubicle doors. Resetting shall be possible without opening relay cases.

## 6. Auxiliary Supply

The supply of all static relays shall be provided by AC/DC converters, preferably for each individual functional unit. Basically, Main and Backup, or duplicated protection systems of the same network element, shall be supplied from different DC circuits. The relay cubicle DC supply shall be monitored and a central alarm issued whenever the voltage exceeds the limits for reliable operation. Schemes shall be based on the fail-safe principle, e.g. DC supply loss or open circuit shall not cause incorrect opening or closing of relay contacts.

If not stated otherwise, the following basic design data for the 220 kV and 20 kV bays of the Qush Tepa and Darzaab substations apply:

- DC trip/control voltage: 220 V DC (+10% ... –30%)

- VT phase secondary voltage: 110 V

- CT phase secondary current: 1 A

- rated frequency: 50 Hz (–6% ... +2%)

Within the specified DC voltage and frequency variations, the offered relays shall retain their rated characteristic accuracy and full operation capability.

## 7. Tripping Circuits

The trip contacts shall be hardwired and act via tripping relays on the trip coils of the relevant circuit breaker. Two tripping relays with remote reset via the station controller shall be implemented, with one trip relay combining the Main protection relays and the second combining the Backup protection relays. Each trip relay shall act on a separate trip coil of the circuit breaker.

The trip output of individual protection functional assemblies shall be of electromechanical type.

The trip circuits shall be continuously supervised in the closed and open position of the circuit breakers. The trip supervision circuit shall include, to the extent feasible, all loops between trip contacts.

## 8. Electromagnetic Interference, Insulation

All the necessary measures at substation/control building/cubicle level for ensuring proper function and component safety of the offered relay types with respect to over-voltages induced in the secondary wiring (from primary and secondary equipment switching), such as shielding and earthing of control cables, are part of the scope.

The relay equipment shall meet the following specifications as a minimum:

- HV test: 2 kV 50 Hz, 1 min or 2.8 kV DC 1 min

- HV impulse: IEC 60255-4/5, Class III, test voltage 5 kV

- HF test: IEC 60255-22-1, Class III

- Electrostatic discharge: IEC 60255-22-2, Class III

- Radiated electromagnetic field: IEC 60255-22-3, Class III

- Fast transient tests: IEC 60255-22-4, Class IV

- Temperature: IEC 60068-2-1, –5°C, 96 hours; IEC 60068-2-2, Class +55°C, 96 hours

- Relative humidity: IEC 60068-2-3 with severity class 56 days

- Enclosure: IEC 60529, IP 54

- Vibration: IEC 60255-21-1, Class 1

- Shock & bump: IEC 60255-21-2, Class 1

- Seismic: IEC 60255-21-3, Class 3

Signal interfaces between protection equipment and switchgear or communication equipment shall be of the opto-coupler type.

To minimize transient over-voltages in measuring, control, alarm and instrument transformer cables, the “Recommendation for measures to minimize transient over-voltages in secondary conductors inside of High Voltage Substations”, VDEW (Association of German Electricity Corporations), 1992, shall be applicable.

## 9. Quality Assurance

Type tests

Approved type tests, reports or certificates and documentation shall be available for each functional assembly of the proposed protection systems, similar in all essential respects to the equipment included in the Contract. Submittal of complete test records may be required by the Employer. If not relevant for the actual service conditions, the Employer reserves the right to require re-testing or additional tests to be included in the routine test program.

Factory acceptance tests

Equipment for modular static protection systems (e.g. distance, busbar protection etc.) pre-assembled in the relevant boards/cubicles etc. shall be tested in the Contractor's workshops as far as wiring and proper function is concerned. Simulated inputs (binary signals, current and voltage inputs from test power supplies) shall be used for the tests.

The Employer reserves the right to attend the factory tests for the main protection equipment.

Software updating

The Employer reserves the right to attend the factory tests for software testing/updating of the main protection equipment.

Commissioning tests

The commissioning test program shall be submitted to the Employer and the Employer's Representative for approval. Minimum test requirements are as follows.

Current transformers

General check of insulators, earth connections and terminal identification. Magnetization curve, polarity, ratio, secondary resistance tests, insulation resistance tests.

Protection basic tests

Insulation resistance of all secondary circuits (current and voltage transformers, control, indication and alarm circuits, etc.).

Primary injection of current transformer circuits, including overall injection of differential protection circuits, to prove all connections and to check ratios, fault settings, stability and phase identification.

Secondary injection of AC and DC relays to check their operating characteristics.

Voltage transformers

General check of insulators, earth connection and terminal identification. H.V. tests, ratio, polarity, measurement of insulation resistance and winding resistance, magnetizing currents.

Secondary injection of voltage transformer circuits

Secondary injection of VT circuits. Measurements of voltage at each point of the VT secondary circuit by applying 100 V to this circuit.

Check of schemes

Complete functional tests of tripping, alarm, control and indication circuits. Operation of tripping elements at reduced DC voltage.

Phasing tests of main plant prior to making alive.

Measurement of the end-to-end line differential and tele-protection channel transmission times between the Qush Tepa and Darzaab substations, and to any other interconnected station.

Simulation by secondary injection and signal transmission of the various protection transferred trips, phase-segregated differential protection trips and all auto-reclosing programs with their associated breakers.

Load tests for protections and directional units.

## 10. Main Equipment Design for Protection and Control Equipment

### 10.1 Serial Interfacing of Relays

All relays shall be equipped with the necessary interface cards to enable connection of the relays to a Substation Control and Monitoring System (SCMS) IEC 61850-8 bus, including future expansions. The control and protection relays provided shall be capable of accepting commands from, and returning analogue and digital data to, the station controller of the substation automation system.

All signals, alarms, trips and faults will be reported via fiber optic connection to the automation system. It shall also be possible to change pre-set parameter sets for each individual relay from the station automation workstation. The serial working interface for asynchronous transmission shall have a Hamming distance of 4.

Initially, all control and protection relay inputs and outputs shall be to/from the substation SCADA RTU to be supplied under this contract.

Other required serial interfacing:

- system interface, potential-free, suitable for asynchronous connection via local fiber optic connection to the central systems; all devices, connectors and fiber optic connections;

- operator interface for parameterization, setting, and retrieving of stored event records via hand-terminal or PC; the appropriate software and PC are part of this supply.

The working and system interfaces and the associated interface devices shall withstand all insulation tests as specified.

### 10.2 Line Differential Protection Including Auto-reclosing

Line differential protection relays use fiber cable (in OPGW) for connection to the remote end relay. Dedicated OPGW equipment is provided under this contract for the coupling to the remote ends, i.e. between the Qush Tepa and Darzaab substations and their respective connecting substations. All necessary additional devices, plug connectors, conventional and short copper are part of this supply. The selection of the equipment shall be done so as to allow for 20% attenuation reserve in the end-to-end transmission. All necessary additional devices (transmitter-receivers), plug connectors, conventional and short copper or fiber optic connections up to the terminals of the fiber optic cable shall be part of this supply.

These line differential protections shall be a digital unit protection, working on the current differential measuring principle, suitable for the EHV transmission systems, featuring:

- phase-selective measuring units and trip outputs;

- adjustable sensitivity for phase and earth faults;

- typical operating time (twice the set value) max. 30 ms;

- transfer trip in case of one-sided fault infeed;

- max. 20 ms total transmission time, opto-coupler input;

- IN/OUT switch for transfer trip feature.

If required, matching interposing transformers shall be part of the supply. The relay shall be built with serial communication for direct connection with the control system and a second serial communication designated for indirect communication with the protection monitoring center. Both communications shall have the possibility to apply IEC 61850 protocols.

The protection shall be a digital relay working on the phase current differential principle, for each end of the protected line. These relays shall cover phase and earth faults, be connected to a different CT core to the backup protection, and be suitable for the protection of HV transmission lines with a minimum of 3 ends, featuring basically:

- phase-selective measuring units and trip outputs;

- phase-segregated trip not required;

- adjustable sensitivity for phase and earth faults;

- typical operating time (twice the set value) max. 30 ms;

- transfer trip in case of one-sided fault infeed;

- IN/OUT switch for transfer feature; IN/OUT switch for protection.

2-phase O/C and E/F check features are to be provided to prevent the tripping of the circuit breaker if local end fault current is absent. IN/OUT switch for current check feature and inter-tripping scheme shall be provided.

Other features must include:

- backup protection (distance or overcurrent time function);

- self-supervision of the main hardware components and of the communication to the remote end; the “device faulty” and “channel faulty” alarms shall be made available to the SCMS and shall be locally LED-indicated; the “channel faulty” alarm shall be time-delayed (1 ... 50 s);

- fault locator;

- local LED indications (seal-in) or readable on the LCD display, including: in operation (green); device faulty (red); channel faulty (red); direct transfer trip (red); trip (red); resetting by local push-button or via the centralized Substation Control and Monitoring System (SCMS).

Typical alarms available initially to the RTU, and in the SCMS, shall include:

- device faulty; channel faulty; trip;

- disturbance and event recording, cyclic overwriting, minimum event time 2 s, with pre-fault history, transferable to the SCMS on request or retrievable menu-guided from the PC; the event recording shall be time-tagged by an included real-time clock synchronized to the SCMS;

- settings, parameters and event records shall be stored in a non-volatile memory (at least three successive events capability);

- one-end test facilities, display of the phase and zero-sequence service currents;

- external switch with the positions IN/OUT (trip circuits interrupted); heavy duty trip contacts suitable for double-pole direct trip with station battery voltage of the main circuit breaker;

- Main-2 (Backup) protection IN/OUT switch to be provided to isolate the tripping circuit.

Auto-reclosing Scheme

The described protection scheme (function) shall initiate an auto-reclosing cycle, featuring at least the following selectable cycles:

- one-phase AR by one-phase faults;

- three-phase AR by multiphase, all kinds of faults, and after unsuccessful one-phase AR;

- auto-reclosing out of service.

Dead time for the three-phase AR cycle shall be independently and continuously adjustable. The device shall be provided with the following selectable (from control room) checking facilities:

- dead line/live bus;

- dead bus/live line;

- synchro-check.

The scope of supply includes all necessary time/auxiliary relays etc. external to the AR device necessary to complete the above operational features.

The AR function shall be provided with the possibility of external blocking in case of:

- manual closing of the line;

- delayed trips (backup zones);

- busbar and breaker-failure protection operation;

- circuit breaker interlocks.

The scheme shall be provided with the following local indications: auto-reclosing blocked; auto-reclosing initiated; auto-reclosing out of service; auto-reclosing in progress. All inputs from binary equipment (circuit breakers) shall be provided with opto-couplers.

### 10.3 Distance Protection (Function) Including Auto-Reclosing

The protection shall be a digital distance relay for phase and earth faults, connected (where possible) to a different CT core than the main protection (for the one-side-supplied OHL – backup protection), suitable for the protection of the 220 kV HV transmission lines of the Qush Tepa and Darzaab substations, featuring basically:

- typical operation time of 1st zone less than 30 ms;

- simultaneous measurement of all fault loops;

- preferably, at least for the earth fault measuring elements, unlimited directional discrimination by cross-polarization and voltage memory;

- appropriate hardware/software measures for correct performance in the presence of CT saturation and CVT transients;

- accurate impedance measurement down to 20% of the rated current;

- separate measuring units for under-reaching Zone 1;

- min. 2 forward measuring backup zones (timer-controlled);

- feature to be accelerated via tele-protection devices;

- 3-phase and 1-phase trip possibility;

- power swing blocking;

- switch-on-to-fault feature;

- fault locator;

- DC supply supervision (local and remote).

Auto-reclosing Scheme

The described protection scheme (function) shall initiate an auto-reclosing cycle featuring at least the following selectable cycles:

- one-phase AR by one-phase faults;

- three-phase AR by multiphase, all kinds of faults, and after unsuccessful one-phase AR;

- auto-reclosing out of service.

Dead times for the three-phase AR cycle shall be independently and continuously adjustable. The device shall be provided with the following selectable (from control room) checking facilities:

- dead line/live bus;

- dead bus/live line;

- synchro-check.

The scope of supply includes all necessary time/auxiliary relays etc. external to the AR device necessary to complete the above operational features.

The AR function shall be provided with the possibility of external blocking in case of:

- manual closing of the line;

- delayed trips (backup zones);

- busbar and breaker-failure protection operation;

- circuit breaker interlocks.

The scheme shall be provided with the following local indications: auto-reclosing blocked; auto-reclosing initiated; auto-reclosing out of service; auto-reclosing in progress. All inputs from binary equipment (circuit breakers) shall be provided with opto-couplers.

### 10.4 Time-Overcurrent Functions

Overcurrent functions and earth fault functions shall be of the definite time lag (DTL) pattern with separately adjustable time and current settings, or inverse definite minimum time (IDMT) pattern. The range of DTL current setting shall be at least 5% to 240% in steps not exceeding 5% for overcurrent functions, and 5% to 80% in steps not exceeding 5% for earth fault functions. Time settings for both overcurrent and earth fault functions shall be adjustable over a range of at least 0.05 to 1.0 times, in steps not exceeding 0.05 times.

Minimum 2 independent definite stages shall be included.

The IDMT protection characteristics shall comply with the latest IEC stipulations and their curves shall be such as to trip after three seconds at ten times the current setting when a time multiplier setting of 100% is applied.

Where directional overcurrent functions are required, a three-pole current element shall be provided, as specified, inoperative until the directional element actuates. The external current and voltage connections to the directional overcurrent phase fault elements shall be arranged so that the phase current in any element is associated with a voltage signal which is derived from the line voltage which lags the current phase by 90° (i.e. 90° relay quadrature connection).

The internal connections of the directional overcurrent element shall be such that the maximum torque in a direction to actuate is produced when the current flowing in the current circuit leads the voltage applied to the voltage circuits by 45° maximum torque angle.

### 10.5 Directional Earth Fault Functions

The directional earth fault functions shall be provided with current fault elements, inoperative until the directional element actuates.

The current signal for the directional earth fault relay shall be derived from the residual circuit. The voltage signal shall be the residual voltage produced by an open delta circuit on the main VT and the voltage input rating shall be compatible with the open delta winding output and primary system earthing.

The protection functions for earth faults shall include the following features:

- directional earth fault protection (definite time earth overcurrent protection with non-directional backup and stand-by protection function; feature to be accelerated via tele-protection devices);

- non-directional inverse time lag overcurrent time protection for earth faults with selectable characteristics.

The directional earth fault protection can be extended by integrated directional comparison logic so that, by means of a carrier channel, fast and selective tripping for high resistance earth faults shall be possible.

### 10.6 Overvoltage Protection Functions

The overvoltage protection relay shall contain the following functions:

- one phase-segregated function (minimum 2 stages);

- one zero-sequence voltage function (minimum 2 stages); the residual voltage shall be measured by an open delta VT winding or shall be calculated internally as 3Uo.

The tripping shall be performed at the local circuit breaker and at the other end (ends) of the line/transformer by sending an inter-tripping signal.

### 10.7 Under Voltage Protection Functions

The under-voltage protection shall protect consumers (including machines) from the consequences of dangerous voltage dips and shall prevent impermissible operating conditions and possible loss of stability.

The under-voltage protection scheme shall contain a one-phase under-voltage detection with a minimum of 2 stages.

The tripping shall be performed at the local circuit breaker and at the other end (ends) of the line/transformer by sending an inter-tripping signal.

### 10.8 Circuit Breaker Failure Protection

The circuit breaker failure protection shall be installed for all 220 kV circuit breakers at the Qush Tepa and Darzaab substations. This protection detects failures of tripping command execution, for example due to a defective circuit breaker.

The current detection logic shall be phase-segregated and shall therefore also be used in single-pole tripping schemes.

If the fault current has not been interrupted after a settable time delay has expired, a re-trip command or the busbar trip command shall be generated.

### 10.9 Under- and Over Frequency Protection Functions

The under- and over-frequency protection function detects abnormally high and low frequencies. If the network frequency lies outside the admissible range, appropriate actions are initiated.

A frequency decrease occurs when the system experiences an increase in real power demand or sub-networks that cannot (or not fast enough) be compensated by additional performance generation. In this case the real power demand has to be decreased by load shedding.

An increase in system frequency occurs when large blocks of load are removed from the system, or again when a malfunction occurs with a generator governor or AGC system.

Under- and over-frequency protection consists of four frequency elements. Each stage is independent and can initiate different control functions. Three frequency stages shall be designed for decreased frequency detection (f<, f<<, f<<<), the fourth shall be an over-frequency stage (f>).

This under- and over-frequency protection shall not operate if voltage or frequency are outside the working range of the frequency protection.

### 10.10 Synchro-check Function

The synchronism and voltage check function shall ensure that the stability of the network will not be endangered when a 220 kV power transformer at either the Qush Tepa or Darzaab substation is switched onto a bus bar. For this purpose, a synchronism check function is provided.

After verification of the network synchronism, the function shall enable the CLOSE command. Alternatively, reclosing shall be enabled for different criteria, e.g. checking that the bus bar or line is not carrying a voltage (dead line or dead bus).

Adjustable values shall be the operating modes, permissible voltage difference, frequency difference and angle difference. The supervision time shall be adjustable, with time steps of 0.01 s.

### 10.11 Overload Protection with Thermal Replica

The overload protection with thermal replica shall be used to prevent thermal overloading of corresponding equipment, e.g. power transformer. The following features shall be included:

- overload calculation using a thermal replica according to IEC 60255-8 without ambient temperature influence;

- overload calculation using a thermal replica according to IEC 60255-8 with ambient temperature influence;

- calculation of the hot-spot temperature and determination of the aging rate according to IEC 60354;

- thermal alarm and trip stages.

### 10.12 Protection Settings Report

The Contractor shall undertake the Protection Setting Report, in which the settings shall be calculated for all protection for this project listed in the Scope of Supply, identifying also any necessary changes in the connected network. In this Report shall also be calculated or checked the settings of other existing non-unit protections (see the definitions of IEV 448 – IEC 60050 (448)) in the 220 kV and 20 kV specified nodes of the Qush Tepa and Darzaab substations which have to be changed in liaison with implementation of new calculated settings.

This Report has to contain the description of all principles of these calculations as well as the entire calculations themselves. The results shall also be shown in one map of selectivity covering the 220 kV – 20 kV networks of both substations.

The available data required for preparation of the protection settings report will be provided by the Employer, as far as available. These data have to be verified by the Contractor and the missing data has to be calculated or estimated. The Contractor has to provide, in due time, a list with the required data.

# Chapter 12

# Qush Tepa and Darzaab Substations SCADA and Communication System

# Qush Tepa 220/20 kV Substation and Darzaab 220/20 kV Substation

# RTU Requirements & Specifications

## 1. Brief Description

The RTU gathers digital and analog signals and supplies these data over a variety of industry-standard protocols to a control and supervisory data acquisition center or a local HMI. It needs to have many types of modules to gather many types of signals and shall also be able to perform and distribute logic.

## 2. General Requirements

The RTU needs to be used with protective relays and other IEDs as each substation's SCADA data concentrator, at both the Qush Tepa and Darzaab substations.

It should be able to be configured to collect and view the substation's SER (Sequential Event Recorder) and event reports.

It needs to be fully compatible with all connected devices using standard protocols. It needs to be able to scale values and calculate logic in an IEC 61131 configuration environment.

It needs to include the IEC 61131 logic engine, preconfigured to provide access for all system tags, IEDs, I/O data, diagnostics, alarms, security events, and communication statistics.

It needs to support a module which is equipped with an embedded, integrated web HMI, fully capable of being configured and used in monitoring and control of the power substation-related devices.

Fully integrated modular digital I/O, analog input, measurement data, and control performance in high speed and high accuracy with flexible I/O selections and deterministic performance.

Proportional Integral Derivative (PID) control capability.

Synchronized current and voltage measurements (top-of-second synchronized measurement) which lead to an auto-synchronized system (using multiple CT/PT and I/O modules).

Latest update against cyber-security threats and malware.

Equipped with advanced user authentication and system security.

Enable multiple SCADA connections with multiple HMIs of the same or different substations and National Load-dispatch/Control Centers (NLCCs).

Be able to provide fiber optic connection, besides the serial and Ethernet connections, to communicate with the I/O network.

Support redundant power supply with a wide range in each level of voltage. Power supply modules need to be capable of supporting different voltage supply sources, such as –48 VDC and 220 VDC supply sources.

Needs to support hot-redundant CPUs (control module of the RTU).

Support for more than 50 modules used without loss of speed and determinism.

It needs to have the capability for a digital output module with trip-rated contacts (30 A make and 6 A carry) to limit the need for interposing relays.

Poll data sets and reports from other IEDs with optional IEC 61850 MMS clients.

Standard management of task processing sequence and solve rate.

Optimizable usage of processor by setting processing rate as per the necessities.

Capable of task processing including protocols, I/O, system management and any custom logic programs in the logic engine (also for event-driven tasks) with Structured Text (ST), Ladder Logic Diagram (LD), or Continuous Function Charts (CFC).

Its web-based HMI system needs to have the management capability of user accounts, system alarm configuration (also alarms for analog values which cross a threshold), visualization, mapping (of system and other IEDs' tags), screen creation, and permission assignment. User logs and network policy maintenance should be available to the Administrator. Multiple users should be able to view this web HMI simultaneously.

Its configuration software needs to have the capability for offline and online configuration.

The configuration software needs to have custom device template creation functionality.

Needs to include distributed control strategies, sequential logic, SER report and accurate performance.

Needs to update all I/O and timestamp inputs with 1 ms accuracy.

Needs to provide a system-wide Sequence of Events (SOE) report of any tag values' logs, with ODBC database transferability of these logs.

## 3. Technical Requirements

Detailed RTU technical data, communication port specifications, power coupler requirements, and opto-isolated control input requirements applicable to the Qush Tepa and Darzaab substations shall be as set out in the corresponding Schedule of Technical Data and Technical Data Sheets (Appendix-1), to be duly completed by the Bidder as proof of compliance.

# Telecommunication Requirements & Specifications

## 1. Telecommunication through Fiber Optic (SDH & DWDM with OTN)

### 1.1 Scope

This section covers the requirements for the fiber optic telecommunication system (SDH and DWDM with OTN) connecting the Qush Tepa and Darzaab substations to each other and to the National Power Grid communication network, in support of protection, SCADA, teleprotection and voice/data services.

### 1.2 General Features

The general features of the fiber optic telecommunication system, teleprotection of power transmission lines, PABX, VHF communication between switchyards and local control centers for maintenance works, and the power quality meter (PQM) requirements shall be as detailed in the Schedule of Technical Data and Technical Data Sheets (Appendix-1) applicable to the Qush Tepa and Darzaab 220/20 kV Substations, duly completed by the Bidder as proof of compliance.

## 2. Teleprotection – Tele-protection of Power Transmission Lines

Teleprotection channels shall be provided for the 220 kV transmission lines associated with the Qush Tepa and Darzaab substations, in coordination with the line differential and distance protection functions described in Section B1.8, to ensure fast and selective clearance of faults on the interconnecting transmission lines.

## 3. PABX

A Private Automatic Branch Exchange (PABX) system shall be provided at each substation to support internal and external voice communication requirements for operation and maintenance personnel.

## 4. VHF for Communication between Switchyards & Local Control Centers Maintenance Works

A VHF radio communication system shall be provided to support communication between switchyard personnel and the local control centers during maintenance works at the Qush Tepa and Darzaab substations.

Power Quality Meter (PQM)

Power quality meters shall be provided at the Qush Tepa and Darzaab substations in accordance with the requirements set out in the Schedule of Technical Data, to monitor and record power quality parameters at the relevant metering points.

## 2.  SCADA / REMOTE TERMINAL UNIT (RTU) REQUIREMENTS

### 2.1 General Requirements

The RTU/SCADA equipment supplied for the Qush Tepa and Darzaab Substations shall, at a minimum, meet the following general requirements: The RTU/SCADA equipment supplied for the Qush Tepa and Darzaab Substations shall, at a minimum, meet the following general requirements:

- Capable of Load Shedding for industrial and isolated grids, with power measurement and a logic engine for under-frequency and demand-control load shedding.

- Capable of being used as a master RTU or as a distributed logic device, and able to connect in star, sequential, and hybrid network topologies.

- Support for IEC 61850 GOOSE and Synchro-phasor Concentration capabilities.

- Intelligent port switching capability.

- Capable of being used as a Secure Network Gateway for industrial data concentration.

- At least 2 Ethernet ports per CPU for communication with local and remote HMIs.

### 2.2 Technical Requirements

| Item | Details |
| --- | --- |
| General – Operation | Accurate and real-time capable Operating System |
| General – Operating Temperature Range | –40°C to +85°C |
| CPU Processing & Memory – Processor Speed | To be specified by the Manufacturer; suitable for real-time SCADA/RTU processing loads |
| CPU Processing & Memory – Cache | To be specified by the Manufacturer |
| CPU Processing & Memory – Memory (RAM) | Sufficient for full protocol stack, logic engine, and historical/event buffering |
| CPU Processing & Memory – Storage | Non-volatile storage sized for firmware, configuration, logic, and event/SOE logs |
| Required Security – Account Management | User Accounts, User Roles, LDAP Central Authentication, Strong Passwords, Inactive Account Logout |
| Required Security – Intrusion Detection | Access/Audit Logs, Alarm LED, Alarm Contact |
| Required Security – Encrypted Communication | SSL/TLS, SSH, HTTPS |
| Required Protocols – Client | Must support: DNP3 Serial, DNP3 LAN/WAN, Modbus RTU, Modbus TCP, ASCII, Fast Messaging, IEEE C37.118, IEC 61850 MMS, IEC 60870-5-101/104, SNMP. Preferably: LG 8979, CP2179. |
| Required Protocols – Server | Must support: DNP3 Serial, DNP3 LAN/WAN, Modbus RTU, Modbus TCP, Fast Messaging, IEEE C37.118, IEC 61850 MMS, IEC 60870-5-101/104, FTP, SFTP. Preferably support: SES-92, LG 8979. |
| Required Protocols – Peer-to-Peer | IEC 61850 GOOSE, DNP USRBE, Parallel Redundancy Protocol or equivalent |
| Engineering Access – Modes | Interleaved, Direct |
| Engineering Access – Port Server | Map Serial Ports to IP Ports |
| Engineering Access – Secure Web Server | Diagnostic (of all its modules & functions) and Communications Data |
| Time-Code Input (Modulated IRIG-B) – Input Impedance | 2 kΩ |
| Time-Code Input (Modulated IRIG-B) – Accuracy | 500 µs (at least) |
| Time-Code Input (Modulated IRIG-B) – On (1) State | Vih > 2.2 V |
| Time-Code Input (Modulated IRIG-B) – Off (0) State | Vil < 0.8 V |
| Time-Code Input (Demodulated IRIG-B) – Input Impedance | 2 kΩ |
| Time-Code Input (Demodulated IRIG-B) – Accuracy | 500 ns (at least) |
| Time-Code Input (Demodulated IRIG-B) – On (1) State | Voh > 2.4 V |
| Time-Code Output (IRIG-B) – Off (0) State | Vol < 0.8 V |
| Time-Code Output (IRIG-B) – Load | 50 Ω |
| Network Time Protocol (NTP) Modes – NTP Client | Three or more configurable servers |

### 2.3  Communication Ports

| Item | Details |
| --- | --- |
| Ethernet Ports for Complete Configuration and/or Programming – Ports | ≥ 1 |
| Ethernet Ports for Complete Configuration and/or Programming – Data Rate | Automatic |
| Ethernet Ports for Complete Configuration and/or Programming – Protocols | Dedicated port |
| Ethernet Ports for Communicating to LDC and/or NLCC – Ports | 2 |
| Ethernet Ports for Communicating to LDC and/or NLCC – Data Rate | 10 or 100 Mbps |
| Ethernet Ports for Communicating to Signaling Devices (Protection Relays, etc.) – Connector | RJ45 Female (or SC Fiber 100 Mbps if specified) |
| Ethernet Ports for Communicating to Signaling Devices (Protection Relays, etc.) – Ports | 2 (redundant, consistent with all networking schemas in the SCADA system) |
| Fiber-Optic Ports (Class 1 Laser/LED) – Data Rate | Automatic, 100 Mbps or higher if specified |
| Fiber-Optic Ports (Class 1 Laser/LED) – Connector | RJ45 Female (or SC Fiber 100 Mbps if specified) |
| Fiber-Optic Ports (Class 1 Laser/LED) – Wavelength | 1300 nm (or higher if required/specified) |
| Serial Ports – Optical Connector Type | SC |
| Serial Ports – Fiber Type | Multimode |
| Serial Ports – Link Budget | Around 11 dB |
| Serial Ports – Min. TX Power | Around –20 dBm |
| Serial Ports – Min. RX Sensitivity | Around –30 dBm |
| Serial Ports – Fiber Size | 50–200 µm |
| Serial Ports – Approximate Range | 2 km |
| Serial Ports – Data Rate | 100 Mbps or higher if specified |
| Serial Ports – Typical Fiber Attenuation | –2 dB/km |
| Serial Ports – Ports | 4 |
| Serial Ports – Types | EIA-232 & EIA-485 supported (software selectable) |
| Serial Ports – Data Rate | 300 to 115200 bps |
| Serial Ports – Connector | DB-9 Female |
| Serial Ports – Time Synchronization | IRIG-B |
| USB Ports – Power | +5 Vdc on Pin 1 (500 mA maximum) |
| USB Ports – Device Ports | 1 × Type B |

### 2.4  Power Coupler

| Item | Details |
| --- | --- |
| Typical Fiber – Attenuation | –2 dB/km |
| AC Power Supply (High-Voltage Model) – Nominal Supply Voltage | 120–240 Vac, 50 Hz |
| DC Input Voltage (High-Voltage Model) – Nominal Supply Voltage | 125–250 Vdc |
| DC Input Voltage (High-Voltage Model) – Operational Voltage Range | 85–300 Vdc |
| AC Input Voltage (High-Voltage Model) – Operational Voltage Range | 85–264 Vac, 40–70 Hz |
| DC Input Voltage (Low-Voltage Model) – Nominal Supply Voltage | 4–48 Vdc |
| DC Input Voltage (Low-Voltage Model) – Operational Voltage Range | 19.1–57.6 Vdc, polarity dependent |

### 2.5 Opto-Isolated Control Inputs

The RTU's opto-isolated control inputs and outputs shall meet the following pick-up/drop-out requirements when used with DC and AC control signals:

| Category | Item | Details |
| --- | --- | --- |
| When Used With DC Control Signals | 250 Vdc | ON for 200–275 Vdc / OFF below 150 Vdc |
|  | 220 Vdc | ON for 176–242 Vdc / OFF below 132 Vdc |
|  | 125 Vdc | ON for 100–135.5 Vdc / OFF below 75 Vdc |
|  | 220 Vdc | ON for 88–121 Vdc / OFF below 66 Vdc |
|  | 48 Vdc | ON for 38.4–52.8 Vdc / OFF below 28.8 Vdc |
|  | 24 Vdc | ON for 15–30 Vdc / OFF for < 10 Vdc |
| When Used With AC Control Signals | 250 Vac | ON for 170.6–300 Vac / OFF below 106 Vac |
|  | 220 Vac | ON for 150.3–264 Vac / OFF below 93.2 Vac |
|  | 125 Vac | ON for 85–150 Vac / OFF below 53 Vac |
|  | 220 Vac | ON for 75.1–132 Vac / OFF below 46.6 Vac |
|  | 48 Vac | ON for 32.8–60 Vac / OFF below 20.3 Vac |
|  | 24 Vac | ON for 14–27 Vac / OFF for < 5 Vac |

| Item | Details |
| --- | --- |
| Current Draw at Nominal DC Voltage | 2–4 mA (except for 24 V, 8 mA) |
| Rated Insulation Voltage | 300 Vac |
| Rated Impulse Withstand Voltage (Uimp) | 4000 V |
| Control Outputs (Standard Contacts) – Mechanical Durability | 10 million no-load operations |
| AC Metering – Frequency | 50/60 Hz |
| AC Metering – Voltage Inputs Range (AC Mode) | 45–65 Hz |
| AC Metering – Typical Accuracy | ±0.005 Hz above 20 V |
| AC Metering – Worst-Case Accuracy | ±0.01 Hz above 20 V |
| Sequence Components – Phase Rotation | ABC, ACB |
| Sequence Components – Values | I0, I1, I2, V0, V1, V2 |
| Sequence Components – Typical Accuracy (Magnitude/Angle) | ±0.2% and ±0.2° @ fNOM and V > 6.7 V, I > 0.6 A |
| Sequence Components – Worst-Case Accuracy (Magnitude/Angle) | ±3% and ±0.2° @ fNOM and V > 6.7 V, I > 0.6 A |
| Power / Power Factor (Per Phase & Three-Phase) – Typical Accuracy | 0.1% @ PF > 0.1 / 0.1% @ PF < 0.9 |
| Power / Power Factor (Per Phase & Three-Phase) – Worst-Case Accuracy | 2% |
| Synchrophasor – Conformance | IEEE C37.118.1-2011 as amended by IEEE C37.118.1a-2014 |
| Synchrophasor – Accuracy | Level 1 as specified by IEEE C37.118 |
| Synchrophasor – Measurements | Software selectable – Voltage (VA, VB, VC, VS), Current (IA, IB, IC, IN), Positive-Sequence (V1, I1), Frequency and df/dt |
| Synchrophasor – Processing Rate | 120 Hz |

### 2.6  Abbreviations

| Item | Details |
| --- | --- |
| NLCC | National Load Control Center |
| SCADA | Supervisory Control and Data Acquisition |
| RTU | Remote Terminal Unit |
| HMI | Human Machine Interface |
| IED | Intelligent Electronic Device |
| SER | Sequential Events Recorder |
| IEC | International Electrotechnical Commission |
| PID | Proportional Integral Derivative |
| CT | Current Transformer |
| PT | Potential Transformer |
| ST | Structured Text |
| LD | Logic Diagram |
| CFC | Continuous Functional Charts |
| SOE | Sequence of Event |
| ODBC | Open Database Connectivity |
| DDR | Double Data Rate |
| ECC | Error Correcting Code |
| LDAP | Lightweight Directory Access Protocol |
| DNP | Distributed Network Protocol |
| TCP | Transmission Control Protocol |
| LED | Light-Emitting Diode |
| SSL | Secure Socket Layer |
| TLS | Transport Layer Security |
| SSH | Secure Shell |
| HTTPS | Hyper Text Transfer Protocol Secure |
| FTP | File Transfer Protocol |
| SFTP | SSH File Transfer Protocol |
| ASCII | American Standard Code for Information Interchange |
| SNMP | Simple Network Management Protocol |
| I/O | Input / Output |
| IRIG | Inter-Range Instrumentation Group |
| MHz | Mega Hertz |
| GHz | Giga Hertz |
| MB | Mega Byte |
| GB | Giga Byte |
| Mbps | Mega bit per second |
| RJ45 | Registered Jack-45 |

## 3.  TELECOMMUNICATION REQUIREMENTS & SPECIFICATIONS

### 3.1 Telecommunication through Fiber Optic (SDH & DWDM with OTN)

#### 3.1.1 Scope

Telecom devices supplied for the Qush Tepa and Darzaab Substations shall fulfill the Employer's telecommunication requirements in order to become part of, or connect with, the DABS National Telecommunication Network. The telecom device shall support SDH and WDM (DWDM & CWDM), STM-16/64 SDH Multiplexer, and a compact POTP platform targeted for deployment in the edge and access part of the transport network. It shall be configurable both as a TDM MSPP and as a Packet Switch, shall support both TDM and Ethernet as line interfaces, shall offer full redundancy, and shall come with an expansion chassis for deployment in high-drop locations. It shall be suitable for point-to-point, linear, ring, T, and mesh network topologies, with at least 10 years of spare-parts warranty.

#### 3.1.2 General Features

- POTP: Transition from 100% TDM to 100% Packet, deployable as a TDM MSPP in SDH/DWDM networks transporting data using GFP and LCAS, and configurable as a Packet Switch in Ethernet-based networks offering TDM services through circuit emulation, allowing gradual migration from TDM- to packet-based services.

- Flexibility: A modular architecture with base-chassis variants of 1-unit and n-unit slot counts, an expansion chassis, and a range of TDM and Packet line cards to allow the optimal configuration for each requirement.

- Server Layer: MPLS-TP based pseudo-wires for traffic-engineered flows on trunks, with end-to-end sub-50 ms path-level protection per ITU-T G.8031 on MPLS-TP tunnels.

- Ethernet Features: Best-in-class packet switching with ingress rate limiting, packet classification, 8 CoS queues, scheduling algorithms, and ERPS (Ethernet Ring Protection Switching, ITU-T G.8032) providing 50 ms protected packet rings with support for multiple ringlets and ring topologies.

- Packet Synchronization: Support for SyncE and IEEE 1588v2 for distribution of synchronization information over packet networks.

- Circuit Emulation: Support for SAToP and CESoPSN for carrying legacy TDM traffic over a packet infrastructure.

- EOW: 64 kbps voice channel / Engineering Order Wire between network elements over the SDH overhead, configurable as a shared line with band DTMF signaling and integrated DTMF decoding, based on VoIP.

- EMS: Collection and presentation of management data from geographically dispersed network elements at a centralized NOC, based on the OSI FCAPS model (Fault, Configuration, Accounting, Performance, and Security Management) per TMN functionality.

- Alarms: Alarms (Loss of Signal, Loss of Frame, Remote Defect Indication, Trace Identifier Mismatch, etc.) classified by severity — Critical, Major, Minor, Warning — with a user-based security module assigning read/write/delete permissions per user role.

#### 3.1.3 Equipment Protection

| Item | Details |
| --- | --- |
| Equipment-Level Protection | Cross-connect 1+1 backup, control board 1+1 backup, power 1+1 backup, clock 1+1 backup |
| MPLS-TP Based Service Protection | LSP/PW linear protection, ring protection, anti-multi-failure protection based on MS-PW, LAG, MC-LAG, dual-homing protection, LPT |
| SDH Based Service Protection | 2/4-fiber MS-SP Ring; 1+1/1:n (n ≤ 14) Linear MSP; SNCP/SNCMP/SNCTP; 1:N tributary protection for E1/T1, E3/T3, E4, STM-1(e) and FE |

#### 3.1.4 Ethernet Switching

- VLAN Switching (IEEE 802.1Q)

- Provider Bridges (802.1ad)

- Ingress Rate Limiting at 64 kbps granularity

- Programmable Committed and Peak Rates

- Programmable Committed and Peak Burst sizes

- Egress rate shaping on all ports

- Optical Ethernet connection 1000Base-LX/SX and 100Base-FX

- WAN Protocols: PPP, MLPPP

- Multi-Protocol Label Switching – Transport Profile (MPLS-TP), Spanning Tree Protocol (STP), Link Layer Discovery Protocol (LLDP)

- 8 classes of service as per IEEE 802.1p

- 2-Rate, 3-color marking

- Circuit Emulation

- Port Mirroring

#### 3.1.5 Network Protection

- Ethernet Linear Protection Scheme

- Ethernet Ring Protection Scheme

- LCAS protection for Ethernet

- SNCP, 1+1 MSP for TDM Interfaces

#### 3.1.6 Equipment Redundancy, Ethernet over SDH, Operation & Management

- Power Supply Redundancy; E1 tributary card redundancy; XC (cross-connect) and Aggregate Card Redundancy

- Ethernet over SDH: VCAT per ITU-T G.707; GFP-F mapping per ITU-T G.7041; LCAS per ITU-T G.7042; 64 ms differential delay; graceful degradation in Signal Fail/Signal Degrade

- Operation & Troubleshooting: Performance Monitoring; Remote Software Download; CFM per 802.1ag; Performance statistics for Ethernet & VCGs; User-configurable Local/Remote loop

- Management: Network Management System; SNMPv2 interface; end-to-end management across the SDH POTP family; full remote management over TCP/IP; web-based local/remote management; V.24/V.28 modem interface for remote management

- Synchronization: SyncE; IEEE 1588v2; STMn; E1; 2 Mbps BITS Clock; 2 MHz TTL Clock; HoldOver; internal oscillator

#### 3.1.7 Applicable ITU-T Standards

The equipment shall comply with the applicable ITU-T Recommendations, including but not limited to: G.652, G.655, G.661, G.662, G.663, G.671, G.691, G.692, G.694.1, G.694.2, G.702, G.703, G.704, G.706, G.707, G.7041, G.7042, G.773, G.774 series, G.775, G.7710, G.780, G.781, G.783, G.784, G.801, G.803, G.805, G.806, G.808.1, G.810, G.811, G.812, G.813, G.821–G.826, G.828, G.829, G.831, G.841, G.842, and G.957.

#### 3.1.8  Device Units and Functions

| Category | Item | Details |
| --- | --- | --- |
| SDH Interface Unit | Processing Board | Access and process STM-4 optical signals |
|  | Interface Board | Access STM-4 optical/electrical signals |
|  | Protection Switching Board | Provide TPS protection for STM signals |
| PDH Interface Unit | Processing Board | Access and process E1/T1/STM-1 PDH electrical signals |
|  | Interface Board | Provide service for PDH signals |
|  | Protection Switching Board | Provide TPS protection for PDH signals |
| 63E1 Unit | Processing / Interface / Protection Boards | Access, provide, and protect PRI signals |
| Ethernet Interface Unit | Processing / Interface / Protection Boards | Access and process 10GE, GE, FE Ethernet signals with TPS protection |
| STM-4 SFP Module | — | Up to 4 modules to route between substations for STM-4, transmitting over 80–150 km without a booster |
| ATM Interface Unit | — | Access and process STM-4, STM-1, and IMA E1 ATM signals |
| DWDM Unit | — | Add/drop and multiplex adjacent wavelengths; access DWDM wavelengths; convert client-side wavelengths to standard wavelengths; filter and isolate optical signals from the ROP board |
| SDH Cross-Connect Matrix Unit | — | Cross-connect SDH and PDH signals |
| Synchronous Timing Unit (PCM) | — | Provide system clock for the equipment |
| Overhead Processing Unit | — | Process overhead of SDH signals; interfaces incl. FXS/FXO, 2/4-wire audio and E&M, X.21/V.35/V.11/V.24/V.28, RS232/RS422, RS449/RS423A/RS422A, RS530/RS530A, RS485, G.703 64 kb/s co-directional, IEEE C37.94 |
| Power Interface Unit | — | Access power supply and protect the equipment against abnormal power; 48 Vdc and 220 Vdc |
| Auxiliary Interface Unit | — | Provide various administration and maintenance interfaces |
| Fan Unit | — | Dissipate heat for the system |

### 3.2  Teleprotection of Power Transmission Lines

#### 3.2.1  Scope

Due to the reliability and continuity requirements of the Qush Tepa and Darzaab 220 kV transmission lines, the substations' current-carrying infrastructure shall be protected using teleprotection equipment operating over PLCC and SDH optical networks, connected to the DABS National Grid telecommunication network.

#### 3.2.2  General Features

- Unrivaled speed, security, and reliability.

- Use in a standalone, point-to-point application over IEEE C37.94; IP/MPLS; E1 and G.703 64 kbps transmission links.

- Use as an integrated part of the E1 Voice and Data Multiplexer solution over an SDH or PDH data network.

- 1+1 Route/Path Protection when used as an integrated part of the E1 Voice and Data Multiplexer solution over an SDH or PDH data network.

- Compact, standard 19-inch rack-mountable chassis.

- Bi-directional transmission of 8 command inputs and 8 command outputs; 8-channel trip-counter display.

- Full duplex operation with automatic loop-test facility.

- User-programmable for Direct Tripping, Permissive Tripping, and Blocking Protection Schemes (distance teleprotection).

- SNMPv2 management protocol for management and monitoring.

- Optional IEC 61850 GOOSE support; PSCH.1 Distance Protection Scheme per IEC 61850.

- IEEE C37.94-compliant multi-mode optical link interface option for short-reach links.

- IEEE C37.94-compliant (modulation only) single-mode optical link interface option for long-reach links (≤ 40 km, ≤ 80 km, ≤ 120 km, ≤ 150 km).

- IP/MPLS network interface providing “Distance Protection” over an IP/MPLS network.

- 64 kbps G.703 co-directional and 2.048 Mbps G.703 interface options for transmission over 4-wire electrical links.

- 1+1 redundant optical path protection / route protection, with automatic fail-over switching between E1 + C37.94 or C37.94 + C37.94 optical interfaces.

- Voltage command configurations of 24 Vdc, 48 Vdc, 110 Vdc, 220 Vdc, 250 Vdc, 110 Vac, and 220 Vac.

#### 3.2.3  Performance

- Less than 4 ms relay operating time.

- Less than 6 ms back-to-back operating time (including relay operating time) over the IEEE C37.94 optical interface.

- Less than 7 ms back-to-back operating time over the IP/MPLS interface (typically less than 6 ms).

- Less than 6 ms back-to-back operating time over the 2.048 Mbps E1 interface.

- Less than 7 ms back-to-back operating time over the 64 kbps G.703 co-directional 4-wire data interface.

#### 3.2.4  Flexibility, Maintenance, Logging and Reliability

- User-programmable command holding delay and command sampling rate for error-resistant command inputs and transmission.

- Manual Loop Test, Automatic Loop Test, and end-to-end Delay Measurement Test between the Local and Remote teleprotection terminals.

- Time-stamped alarm and event logging, with IRIG-B, NTP, or IEEE 1588v2 time synchronization options.

- RS232 serial and USB serial interfaces for local terminal access; 10/100BaseT Ethernet interface for remote access; encrypted password protection; Telnet, Web Interface, and SSH for secure remote access; SNMP traps and NMS for real-time monitoring.

- Dry-contact external alarm relay for connection to an annunciator panel (NO or NC configurable).

- Power supply immunity to withstand impulse surges and transients up to 10,000 V; high-quality relays withstanding 10 kV between coil and contacts (1.2 × 50 µs); 2.5 kV RMS contact I/O hi-pot dielectric strength; maximum switching voltage of 400 Vac or 300 Vdc.

- Opto-isolated command inputs and relay outputs, compliant with IEC 255-0-20 / VDE 0435, 0631, 0700, 40013847; mechanical relay life of at least 10,000,000 operations at 18,000 operations/hour.

- Error detection via link-loss detection, LOS detection, line-code violation detection, and block command encoding per IEEE C37.94 for optical links.

#### 3.2.5  Teleprotection Specification

| Item | Details |
| --- | --- |
| I/O | Bi-directional transmission of 8 command inputs and 8 command outputs, configurable to operate selectively or simultaneously over Optical / PDH / SDH network(s) |
| Communication | E1, 2.048 Mbps interface, G.703 64 kbps interface, G.703.1 co-directional interface; IEEE C37.94-compliant multi-mode/single-mode optical fiber interfaces for transmission from 40 km up to 180 km without optical repeaters; teleprotection over IP/MPLS |
| Standalone Integrated Teleprotection | Yes — with transmission interface protocols for IEC 61850 GOOSE over IP/MPLS, IEC 61850 GOOSE over E1 or C37.94, and IEC 60834-1 |
| Synchronization | IRIG-B / NTP time-synchronization option (50-ohm BNC input for IRIG-B) |
| Command Voltages | 110V–125/220–250 Vdc |
| Management | OAM (SNMP/Telnet port RJ45(F)), Serial Port (USB, DB-9 COM), EMS, Graphical User Interface (GUI), NMS |
| Power Supply | 2 × 48 Vdc power supply input (redundant); trip counter display and alarm extension unit may be powered from the teleprotection equipment or directly from 48 Vdc, 110 Vdc, 220 Vdc, or 250 Vdc, with 1+1 redundant power as an option |
| Extras | Installation kit (system core cables, mounting hardware), documentation, user manual |

### 3.3  PABX Exchange / Telephony System

#### 3.3.1  Scope

PABX and other telephony devices provided for the Qush Tepa and Darzaab Substations, which will be part of or connected to the DABS voice communication network, shall fulfill the requirements and expectations of that network as set out below.

#### 3.3.2  General Features

- Provide quality of voice over internet.

- Ability to route (connect directly) a specific analogue or digital number to another specific analogue or digital channel in the local zone or outside (ISDN, PSTN).

- Secure calls; IP-TDM gateway capability; soft-switch capability.

- Integrated H.323 gatekeeper; integrated SIP; integrated FTP client to upload records to an FTP server.

- Efficient traffic management with alternate TDM routes if IP trunk calls fail due to network unavailability.

- Support for numerous system and user features; scalable for future expansions; open architecture for future implementations.

- A seamless mix of IP and traditional phone services; embedded video and audio conferencing; enhanced unified communications and mobility features; lower carriage costs with SIP trunks.

- A rack-mountable chassis that can incorporate telephony, networking, server, and gateway hardware, with the capability to mesh systems into a single-image communication platform.

#### 3.3.3  Standards, Protocols and Coding

The device shall support all applicable ETSI, IETF, and ETS standards for PABX, and at least the following protocols and coding:

- Protocols: SIP / SIPv2, IP, VoIP, ToIP, H.3xx, ITU-T H.323 Version 4, H.225 signaling, RAS, Q.931 call signaling (setup, teardown, disengage), H.245 call control, T.38 FAX relay.

- Coding: G.729, G.711, G.723, RTP / RFC 1889.

- LAN: 10/100BaseT Ethernet port switch, IEEE 802.3/802.3u, auto-sense, automatic cable crossover (MDI/MDI-X), PoE 802.3af (32 W maximum).

#### 3.3.4  Specification

| Item | Details |
| --- | --- |
| Handsets – Digital / Analogue | 5 – 20 |
| Handsets – IP Telephones | 5 – 30 |
| Handsets – SIP | 1 – 3 |
| Handsets – SIP (extended) | 3 – 30 |
| Softphones | 1 – 30 |
| Trunks / Features – Analogue | 32 – 96 |
| Trunks / Features – BRI | 32 – 96 |
| Trunks / Features – PRI | 5 – 10 E1 |
| Trunks / Features – IP Trunks | 5 – 30 |
| Power Supply | 1 × 220 Vac (optional), 1 × 220 Vdc, and 1 × 48 Vdc |
| Gigabit – PoE | Card with 8 ports |

### 3.4  VHF for Communication between Switchyards and Local Control Centers

#### 3.4.1  Scope

For better operation and safety during work and switching operations at the Qush Tepa and Darzaab substations, field staff shall be able to communicate with the control room via VHF equipment. As field staff frequently take instructions from the National Load Control Center (NLCC), the VHF system shall be IP-based and capable of connecting to other substations using telecommunication devices such as SDH and PLCC. The device shall support the latest applicable standards and protocols.

#### 3.4.2  Features

- Radio check, scan lists, scan.

- Vote scan, contacts, settings, call indicator, call log features.

- Call alert operation, emergency operation, text-message features, analog status update, privacy.

- Dual Tone Multi Frequency (DTMF), multi-site controls.

- Security / lone-worker function.

- Password-lock features, notification list utilities.

- Front Panel Programming (FPP).

#### 3.4.3  Specification

| Item | Details |
| --- | --- |
| Digital / Analog / Dual Mode | Digital / Analog |
| VHF / UHF | VHF, UHF |
| Channels | 1000 |
| Power | 1–5 W VHF, 1–4 W UHF |
| Frequency | 136–174 MHz (VHF) / 403–512 MHz (UHF) |
| Estimated Battery Life | 15 to 29 hours |
| Waterproof | IP68 |
| Extended Warranty | Three years |
| Routing | Device shall be able to connect to outside VHF devices using PLCC or SDH |

## 4.  POWER QUALITY METER (PQM)

### 4.1  Brief Description

The Power Quality Meter (PQM) supplied for the Qush Tepa and Darzaab Substations shall provide continuous monitoring of a three-phase system, including metering for current, voltage, real & reactive power, energy use, cost of power, power factor, and frequency. It shall be capable of programmable set points and shall provide assignable output relays to allow control functions to be added for specific applications, such as capacitor power-factor correction control, whenever required.

### 4.2  General Requirements

- High-accuracy revenue metering compliant with ANSI C12.20-2015 0.1 and IEC 62053-22:2003 0.2 accuracy class requirements.

- Capture every power-quality disturbance with preconfigured logs and triggers.

- Compare power-quality measurements across the system with IEC 61000-4-30 Class A power-quality compliance.

- Capture and log multiple years of data with 512 logging channels, more than 10,000 event reports, and more than 100,000 voltage events with around 1 GB storage.

- Perform real-time monitoring of the power system with IEEE C37.118-2014 compliant synchrophasor data.

- Integrate with copper or fiber-optic Ethernet, serial, multidrop, infrared, or telephone-modem communications.

- Simultaneously communicate with multiple devices using the supported communication protocols.

- Synchronize metering time to IRIG-B, DNP3, Modbus, SNTP, or manual input.

- Capable of being upgraded over serial and Ethernet ports using digitally signed firmware files.

- Start metering in less than five seconds after power-up.

- 4-quadrant metering with multiple load-profile recorders; calibration certificate available.

- Accuracy test results shall be equal to or less than 0.025% in both ANSI 0.1 and IEC 0.2 accuracy class requirements, or less than 0.07% Wh guarantee.

- NEMA enclosure options; real-time synchrophasor data per IEEE C37.118-2014.

- Communication protocols: Modbus RTU/TCP, TCP/IP, DNP3 Serial and LAN/WAN, IEC 61850, IEEE C37.118.2, SNTP, FTP.

- Transformer/line-loss compensation capable of removing the magnitude and phase error introduced by CTs and PTs.

- Simultaneous meter and power-quality logging of 512 data channels via a high-speed independent load-profile recorder, trending averages, minimums, maximums, changes, and snapshots at a rate of once every 3 seconds or less.

### 4.3  Measurement and Recording Capability

- IEC 61000-4-30 Class A compliant current, voltage, power, frequency, supply-voltage interruptions, dips and swells, harmonics, inter-harmonics, flicker, and harmonic phase angles for voltage and current.

- High-resolution Total Harmonic Distortion (THD), crest factor, up to the 63rd harmonic content, VSSI (correlating system disturbances with voltage sag/swell/interruptions), and symmetrical components (unbalance).

- Storage and reporting of residual voltage, duration, affected phases, CBEMA/ITIC reports, and time stamp of occurrence.

- VSSI settings including trigger thresholds from ±3% to ±100% of the actual value, with automatic recording duration dependent on the length of the voltage excursion.

- Cybersecurity features with more than 2 password levels for meter configuration and data, and port-security settings with more than 2 permission levels providing controlled read and write access to the ports.

- User-programmable logic combining meter calculations, contact inputs (if applicable), remote command inputs (if applicable), and timers to control internal logic and contact outputs (if applicable).

- Capable of supporting a Capacitor Bank Control Program.

### 4.4  Environmental and Electromagnetic Compatibility

| Item | Details |
| --- | --- |
| Operating Temperature | IEC 60068-2-2:1993: –40°C to +85°C |
| Surge Withstand Capability | IEC 60255-22-1:2007: 2.5 kV common mode, 1.0 kV differential mode, 1.0 kV peak common mode on communications ports; IEEE C37.90.1-2002: 2.5 kV oscillatory, 4 kV fast transient |
| Electrostatic Discharge Immunity | IEC 60255-22-2:2008 Severity Level 4 (both polarities at Levels 1–4); IEC 61000-4-2:2008 Severity Level 4 |
| Radiated Electromagnetic Field Immunity | IEC 60255-22-3:2007 / IEC 61000-4-3:2010 Severity Level 10 V/m; ANSI C12.20-1998 Severity Level 15 V/m |
| Electrical Fast Transient Burst Immunity | IEC 61000-4-4:2011, Severity Level 4 kV |
| Surge Immunity | IEC 62052-11:2003, 4 kV for Current, Voltage, and Power Supply Mains; 1 kV for Auxiliary Circuits |
| Conducted Radio Frequency Immunity | IEC 61000-4-6:2008, Severity Level 10 Vrms |
| Vibration Resistance | IEC 60255-21-1:1988 Class 1 Vibration Endurance, Class 2 Vibration Response |
| Shock Resistance | IEC 60255-21-2:1988 Class 1 Shock Withstand, Class 2 Shock Response, Class 1 Bump Withstand |
| Seismic | IEC 60255-21-3:1993 Class 2 Quake Response |

### 4.5  PQM Remote Monitoring and Configuration Software

The PQM shall be supplied with monitoring and configuration software featuring high-level authentication and the latest security updates, enabling the Employer to customize the metering functionalities and retrieve all data from the PQM. The software shall allow setting and editing of meter configuration, settings, and logic; viewing of power-system waveforms (Wave View oscillography) in real time; and checking of wiring connections, phase rotation, voltage & current sequence, and power-flow direction. The software shall support export of meter data in CSV, JSON, or similar formats; automatic generation and export of Meter Reports with VSSI graphing and analysis; Time-of-Use functionality; offline settings development; remote monitoring and reset of real-time metering information; conversion of event reports to oscillography with time-coordinated Device Word bit assertion and phasor/sequence element diagrams; and real-time viewing of voltage and current signals in both time and frequency domains via the Wave View oscillography functionality.

# Chapter 13

# Civil Works, Including Buildings and

# Related Installations

## 1.  General Description of the Project

This section covers the design, construction, and supply of all civil works, including heating, ventilation, and air conditioning, for the new Qush Tepa 220/20 kV Substation and the new Darzaab 220/20 kV Substation, located in Qush Tepa District and Darzaab District, Jawzjan Province, Afghanistan, under the Electrification of Qush Tepa and Darzaab Districts Project of the Ministry of Energy and Water (MEW), Islamic Emirate of Afghanistan (IEA).

The proposed Qush Tepa and Darzaab 220/20 kV substations are designed to connect the two districts to the National Power Grid for the first time, ensuring a reliable electricity supply and supporting sustainable social and economic development in Jawzjan Province. Strategically located along the planned 220 kV transmission corridor, each substation will interconnect the national transmission network with the local 20 kV distribution network, stabilizing voltage levels and improving power quality for residential, commercial, agricultural, and public-sector consumers. Each facility will include a 220 kV switchyard, a 20 kV switchyard, power transformers with high efficiency and modern cooling systems, and advanced protection and control equipment to ensure safe and reliable operation.

State-of-the-art SCADA and communication systems will be integrated to allow remote monitoring and efficient network management from the National/Regional Control Centre. Each substation will feature a robust earthing system and comprehensive lightning protection to enhance safety and resilience against extreme weather events. Additionally, secure boundary fencing, surveillance systems, and fire safety arrangements will be implemented to protect critical assets. Adequate space will be reserved for future expansion, enabling flexibility to accommodate load growth and additional distribution feeders. Construction will adhere to international standards and environmental best practices, minimizing impacts on local communities and ecosystems.

The project aims to create employment opportunities for local residents and support economic growth by providing a stable electricity supply for agriculture, industry, and households. Once operational, the Qush Tepa and Darzaab substations will significantly contribute to the overall energy security and rural electrification goals of Afghanistan.

This document describes quality standards and required functions but is not a fully detailed specification. Therefore, the requirements are not limited to the descriptions given hereafter; items not explicitly mentioned shall be of the same best-quality range as for the entire project.

The civil works must be performed in such a manner that the required high standards of quality and function are fully achieved for both the Qush Tepa Substation and the Darzaab Substation.

Special attention must be paid to aspects specific to the climate and local conditions of Jawzjan Province, including seasonal temperature extremes, wind-blown dust, and the semi-arid soil conditions typical of the region.

The buildings and structures shall be designed with due regard to the need for inspection, maintenance, cleaning, and repair, and must be suitable for long-term operation with a minimum of inspection, adjustment, and repair.

All materials shall be new and of the best quality, suitable for working under the conditions, variations in temperature, and loads encountered in service, without undue distortion, deterioration, or the occurrence of undue stresses in any part, such as to affect the efficiency and reliability of the plant.

## 2.  Scope of Supply and Services

### 2.1  General

The services to be provided within the framework of this specification comprise the planning and complete supply and execution, in every respect, of all civil works required for the faultless operation of the new Qush Tepa 220/20 kV Substation and the new Darzaab 220/20 kV Substation, including all necessary calculations, documentation, prefabrication, delivery, erection, and acceptance.

The civil works consist of, but are not limited to, the following main services, to be executed identically (subject to site-specific adaptation) at both the Qush Tepa Substation and the Darzaab Substation:

- Detailed design and engineering

- Supply of all labor, materials, equipment, temporary works, tools, etc., necessary for the execution of the civil works

- Site-related investigations

- Earthworks, including all leveling and grading works in the project area, as well as the necessary soil improvements as required

- All foundations, including the power transformer foundations

- Structural and non-structural steelwork

- All building works

- Site compound

- Asphalt roads, access road, side ditches, and parking area

- Fencing and gates for the whole switchyard area

- Stormwater drainage and sewage systems

- Civil works for cable routing, ducts, manholes, trenches, tunnels, crossings, etc.

- Fire protection works (fire wall)

- Overhead water tank for the water supply system

- Earthing system

- Pump house

- Landscaping

- Demolition, if required

- Control room building

- Switchyard (220 kV and 20 kV)

- Outdoor lighting system, including street lights

- Boundary wall for each new substation

- RCC or stone masonry retaining wall (if necessary)

### 2.2  The Civil Works in the Substations

All civil works necessary for the complete erection and construction of both new substations are included in the scope.

All civil work within the Qush Tepa 220/20 kV substation facility and the Darzaab 220/20 kV substation facility — including but not limited to the Switchgear Room, Operation Room, kitchen, toilets, Office Room, Battery Room, Workshop Room, Storage Room, restrooms, roads, trenches, drainage, switchyard equipment structures and foundations, boundary wall, fence, gatehouse, overhead water tank, water well, pump house, parking area, landscaping, transformer foundation, and any other building or structure — shall be included.

The control and monitoring systems shall ensure proper functionality, security, and environmental conditions, and each switchyard area shall be under continuous control and monitoring from its respective Control Room.

The access roads to each site are also included in the project scope, from locations to be informed by the Employer.

The discharge of rainwater from each site is also included in the scope of works of the Contractor; the Employer will inform the discharge limits/points for Qush Tepa and Darzaab respectively.

### 2.3  Instructions Related to the Scope of Works

The Contractor will be fully responsible for ensuring that all materials used in the work and temporary works comply with the approved standards, and that all processes of workmanship are carried out with a high degree of efficiency, in accordance with an approved program and compliance with the requirements of the specification. Solely virgin materials shall be used, which have been approved by the Employer/Employer's Representative. While the civil works are in progress at either the Qush Tepa or Darzaab site, the Contractor shall provide suitably qualified, competent civil engineers to be full-time on the site to verify the work, quality, and progress of the subcontractors.

To ensure proper quality assurance, the Contractor shall submit for approval a Civil Works Quality Plan covering both substation sites.

All work shall be constructed to the lines and levels shown on the drawings prepared by the Contractor and approved by the Employer.

The Contractor shall employ competent design engineers to prepare the civil design for both substations. All designs shall be prepared in accordance with the best current engineering practice and with the requirements of the Project Specifications and the appropriate Codes of Practice and Standards approved by the Employer. Any deviation from the Project Specifications must be duly requested and justified in writing by the Employer with formal Design Change Authorizations.

Buildings and structures shall be earthed as specified in the electrical part of the documents.

Ducts, trenches, and/or tunnels shall be provided with suitable permanent pumps and sump pits to enable the easy removal of water spillages and fire-fighting water collected in these areas.

If culvert(s), tunnel(s), trench(es), or any other underground services cross roads, other ducts and channels, etc., these shall be constructed as bridges calculated for heavy truck loading.

Where sizes and/or dimensions are given in the Bidding Package, these shall be considered as informative and for guidance only. The Contractor shall be responsible for finalizing all such sizes and dimensions during detailed engineering to fulfil all functional and specified requirements.

If any items are not specified in the technical specifications, they shall be designed and constructed in accordance with national (Afghanistan) and international standards.

### 2.4  Design and Engineering

Preparation and submission of design calculations and construction drawings by the Contractor to the Employer, for each of the Qush Tepa and Darzaab substations, as follows:

- Piling calculations (if any)

- Structural calculations for buildings, structures, and foundations

- General arrangement and reinforcement drawings for concrete works, including bar bending schedules

- Architectural and structural arrangement drawings and details for the substation building layout, with details of outdoor facilities

- General arrangement and manufacturing drawings for steel structures

- Preparation and submission of drawings for statutory approvals of local authorities and agencies, if applicable

- Calculations for HVAC works, drainage, and sewage systems

### 2.5  Site-Related Surveys

#### 2.5.1  Topographic Survey — Objective

The objective of the topographical survey is to provide accurate and detailed mapping of the proposed Qush Tepa substation site and the proposed Darzaab substation site. The data collected will be used for design, planning, and construction purposes at both locations.

#### 2.5.2  Scope of Work

- Survey the entire project area at each site, including the substation footprint, access roads, drainage areas, and surrounding buffer zones.

- Identify and record all existing features such as buildings, roads, fences, utility lines (overhead and underground), trees, and water bodies.

- Determine ground elevations, slopes, and contours at a maximum interval of 0.5 metres.

- Mark property boundaries and existing benchmarks.

- Provide georeferenced coordinates based on an established national or project-specific coordinate system.

#### 2.5.3  Survey Methodology

- Use Total Station and GPS equipment to collect data.

- Ensure horizontal accuracy within ±5 mm and vertical accuracy within ±8 mm.

- Establish and maintain a minimum of two permanent benchmarks near each site.

- Record data points with a density sufficient to accurately model the terrain, especially in areas with rapid elevation changes.

#### 2.5.4  Deliverables

- Topographical map with contour lines at 0.5 m intervals, for each substation site.

- Location and description of all benchmarks.

- Digital terrain model (DTM) in CAD (.dwg) format.

- Survey report including methodology, equipment used, date of survey, and any encountered issues.

- Hard copy maps scaled appropriately (e.g., 1:500 or 1:1000).

#### 2.5.5  Health, Safety, and Environmental Requirements

- Survey teams must comply with all site-specific health and safety regulations.

- Proper PPE (Personal Protective Equipment) must be used at all times.

- Environmental protection measures should be followed to minimize site disturbance.

#### 2.5.6  Responsibilities

- The Contractor shall ensure the accuracy and completeness of the survey at both sites.

- Any discrepancies found after submission must be corrected by the Contractor at no additional cost.

### 2.6  Soil Investigations

The Contractor shall carry out subsoil investigations of sufficient scope and depth, at both the Qush Tepa site and the Darzaab site, to enable satisfactory determination of all necessary geotechnical characteristics. The investigations must ensure the exclusion of any unacceptable settlement risks and allow for the reliable design, selection, sizing, and execution of foundation systems.

All investigations must be fully completed and reported prior to the commencement of any construction works at the respective site. A detailed specification for the required investigations is provided in Section 6.

### 2.7  Site Development Works

#### 2.7.1  Scope of Work

The scope of site development works shall include, but not necessarily be limited to, the following activities necessary for the preparation, access, and security of each substation site (Qush Tepa and Darzaab):

#### 2.7.2  Site Clearance

The Contractor shall carry out complete site clearance, including removal of vegetation, debris, existing structures, and any other obstructions within the designated boundaries. Diversion, protection, or relocation of existing underground and overhead utilities and services, if encountered, shall be undertaken as required and coordinated with relevant local authorities in Qush Tepa and Darzaab districts.

#### 2.7.3  Site Levelling and Grading

The Contractor shall perform earthworks to achieve the required finished site levels and grades as indicated in the approved design drawings. Works shall include cutting, filling, backfilling, and compaction to specified densities using approved materials.

#### 2.7.4  Construction of Roads, Drainage, and Surfacing

The Contractor shall construct all internal roads, stormwater drainage systems, and surface finishes within each substation premises in accordance with the project specifications, standards, and approved drawings. The works shall include the provision of sub-base, base, surfacing materials, curbs, and necessary road markings.

#### 2.7.5  Temporary Construction Facilities and Enabling Works

The Contractor shall provide, maintain, and subsequently dismantle all temporary facilities necessary for the execution of the works at each site. This includes, but is not limited to, site offices, storage areas, workshops, utilities (water, power, and communication services), and site access arrangements.

#### 2.7.6  Security Fencing

The Contractor shall supply, install, and maintain temporary security fencing around the perimeter of each construction site during the execution phase. Upon completion of the works, the Contractor shall supply and install permanent security fencing in accordance with the approved design and project specifications to safeguard each substation installation.

#### 2.7.7  General Requirements

- All works shall comply with applicable local regulations, utility authority standards, and project-specific technical specifications.

- The Contractor shall take all necessary measures to protect adjacent properties and services during the course of the works.

- Temporary works shall be designed and executed to ensure safety and minimize disruption to ongoing or adjacent operations.

### 2.8  Site Installation and Temporary Works

The Contractor is fully responsible for the design, erection, maintenance, and removal of all temporary facilities and installations required for the proper execution of the project works at both the Qush Tepa and Darzaab sites. All installations shall conform to applicable statutory requirements, environmental regulations, and safety standards.

The Contractor shall supply, at both sites, temporary offices, laboratories, sanitary conveniences, stores, equipment, workshops, compounds, parking areas, etc., necessary for the completion of the works.

#### 2.8.1  Contractor's Organization

- The Contractor shall set up an organization to enable the design, construction, testing, and completion of both substations within the target dates according to the detailed program of works.

- The Contractor shall submit an organization chart including the key personnel for the period of design, construction, and tests on completion, identifying personnel assigned to each of the Qush Tepa and Darzaab sites.

- The Contractor shall periodically revise the organization chart, subject to the approval of the Employer/Project Manager.

#### 2.8.2  Site Establishment

- Site offices for the Contractor and the Employer's representatives at each substation site

- Meeting rooms and document control areas

- Staff welfare facilities (toilets, drinking water, washrooms, rest areas)

- First aid station with certified personnel

- Secure storage areas for materials, tools, and equipment

- Parking areas for vehicles and machinery

- Signage and access control systems

#### 2.8.3  Temporary Utilities

The Contractor shall provide and maintain all temporary utility services required for the execution of the works at each site, including:

- Electricity supply (generator or grid connection) for site operations

- Potable water supply and distribution

- Telecommunications (internet, phone lines)

- Temporary lighting for night-time or low-visibility operations

- Wastewater and solid waste management systems

#### 2.8.4  Documents for the Construction Site

The Contractor shall prepare and provide, in due time and prior to commencement of construction works at each site, the following documents, which require the approval of the Employer/Engineer:

- All necessary general and detailed construction drawings

- Detailed construction time schedule

- Site facilities plans

- Construction Site Regulations

- Environmental protection plan

- Quality assurance plan

- Firefighting and fire protection plan

#### 2.8.5  Site Store

- Each site storage area shall have sufficient surface area so that the process of work is not jeopardized. It shall be fenced and guarded 24 hours a day.

- All materials shall be stored in tiers, stacked, racked, and interlocked/secured to prevent sliding, deterioration, or collapse.

- Maximum safe load limits shall not be exceeded.

- Aisles and passageways shall be kept clear to provide free movement of materials and equipment.

- Each employee working on stored materials in silos, hoppers, tanks, and similar areas shall be equipped with personal fall-arrest equipment.

- Non-compatible materials shall be eliminated from the storage.

- Bagged materials shall be stocked by stepping back the layers and cross-keying the bags at least every 10 bags high.

- Materials shall not be stored on scaffolds.

- Vegetation control shall be exercised when necessary.

#### 2.8.6  Construction Supervision Personnel

The Contractor shall provide a construction supervisory team, for the combined Qush Tepa/Darzaab works, consisting of:

- Senior Construction Manager

- Construction Managers for each section of works (one per substation site, minimum)

- Construction site engineers of various disciplines

- Construction QC Engineer

- Construction Safety Engineer

- Mechanical Engineer

- Electrical Manager

- Construction inspectors

The Senior Construction Manager shall be highly qualified and experienced and will represent the Contractor in all contractual, organizational, and technical matters. All members of the construction supervisory team shall be nominated in writing. Only approved persons will be accepted to perform the site activities.

#### 2.8.7  Final Construction Checks

- At the end of the construction works or of sections at either site, the Contractor shall perform inspections and tests with regard to: completeness, defects, and compliance with the Contract requirements.

- The Contractor shall notify the Employer/Engineer in writing of readiness. Final construction checks shall be conducted jointly. Results will be recorded; deficiency lists shall be prepared if necessary.

- The Contractor has to remedy without delay all deficiencies.

- After successful completion of the works, the Contractor shall submit a final report for each substation.

- Depending on results, the Employer/Engineer may grant or withhold approval for the commencement of test completion of a section or part of the works.

#### 2.8.8  Dismantling and Demobilization

Upon completion of the permanent works at each site, the Contractor shall remove all temporary installations, reinstate the affected areas to their original or specified conditions, and demobilize from the site in a safe and environmentally responsible manner.

## 3.0  Main Civil Works

### 3.1  General Layout

(a) The boundaries and limits of the new Qush Tepa Substation and the new Darzaab Substation are indicated in the conceptual draft general layout drawings provided in the Annexes, one set for each site.

(b) Detailed Arrangement: based on the provided draft layout drawings, the Contractor shall develop and submit a detailed general layout for each substation, incorporating all necessary components for the final configuration. The proposed layouts shall be subject to the review and approval of the Employer or the Employer's Representative.

Design Considerations

In preparing the detailed general layout for each substation, the Contractor shall ensure the following:

- Compliance with all required safety clearances and minimum approach distances for 220 kV and 20 kV equipment.

- Provision of adequate fire compartments and separation zones in accordance with applicable standards.

- Favorable positioning of all plant and equipment to facilitate safe and efficient monitoring, operation, and maintenance activities.

- Consideration of future expansion possibilities (additional 20 kV feeder bays) without disruption to existing operations.

- Full compliance with modern best practices for substation planning and construction.

Entrance Locations

The Contractor shall propose the final locations and configurations of the main and secondary entrances to each substation area. The proposed arrangements shall be submitted for review and approval by the Employer or the Employer's Representative.

General Notes

- The Contractor shall take into account site-specific conditions, access requirements, prevailing wind directions, topography, and other relevant factors when proposing the detailed layout for Qush Tepa and Darzaab respectively.

- Any deviations from the conceptual draft layouts shall be clearly indicated and justified in the Contractor's submission.

- Compartments, favorable layout of the plant components for monitoring and maintenance, possibility for extension, and any other requirements of up-to-date substation construction shall be taken into account.

- The final position of the entrance at each substation area will be proposed by the Contractor and agreed by the Employer or the Employer's Representative.

### 3.2  Control Building

- The roof of the control room shall be constructed of reinforced concrete, with a suitable truss applied on top with a proper slope in accordance with the relevant standards and site conditions, at both the Qush Tepa and Darzaab substations.

- The decision regarding construction of the control building as a single-story or two-story structure shall be determined during the design stage, in coordination with and subject to the approval of the Employer, independently for each site.

- Under the responsibility of the Contractor, along the basic design indicated, all auxiliary, control, protection, and telecommunication equipment for the 220/20 kV switchyards shall be accommodated within the appropriate rooms of the station control building at each site.

- The proposed arrangement of the building can be modified by the Contractor according to the specific conditions (i.e., transport ways, arrangement of the equipment, partition of the building, etc.), subject to the Employer's approval.

- Minimum floor area requirements have been given in the following table, which may be increased, if required, at the time of detailed engineering to suit project requirements.

- An open space of 1 m minimum shall be provided on the periphery of the rows of panel and equipment, generally in order to allow easy operator movement, access, and maintenance.

The following rooms shall be accommodated in the Control Room Building at each of the Qush Tepa and Darzaab substations:

- Battery room

- Office room

- Workshop

- Bedroom

- Change rooms

- Kitchen room

- AC & DC rooms

- Manager room

- Protection and Control Room

- Telecommunication, RTU, Metering, and SCADA rooms (or all in one room)

- Switchgear room

- Corridors

- Toilet and shower room

- Storage room

Minimum Carpet Area Requirement for Various Rooms (per Substation)

| S. No. | Room / Parameter | Description |
| --- | --- | --- |
| 1 | Protection and Control Room | As per detailed engineering |
| 2 | Switchgear room | As per detailed engineering |
| 3 | AC & Battery charger room | As per detailed engineering |
| 4 | Battery room | As per detailed engineering |
| 5 | Storage room | As per detailed engineering |
| 6 | Office room | As per detailed engineering |
| 7 | Kitchen | As per detailed engineering |
| 8 | Bedroom | As per detailed engineering |
| 9 | Change room | As per detailed engineering |
| 10 | Telecommunication, RTU, Metering, and SCADA rooms | As per detailed engineering |
| 11 | Wash room – 2 | As per detailed engineering |
| 12 | Manager room | As per detailed engineering |
| 13 | Corridor | As per detailed engineering |
| 14 | Room for workers | As per detailed engineering |
|  | Total | sq. m, as per design |

Note: The control room area at each substation shall be adequately sized to meet the requirements of the current project scope and shall also allow for potential future expansion without the need for major structural modifications. Proper space planning should ensure functionality, accessibility, and scalability for future needs, and the Employer shall approve the layout plan of the Control Room Building for both Qush Tepa and Darzaab.

Description of the Control Building

- Structure: modular system of reinforced concrete slab, frames, steel truss over the slab, with brick wall infill.

- Foundations: according to the soil report to be prepared by the Contractor for the respective site (Qush Tepa or Darzaab).

- Roof: reinforced concrete with steel truss.

- External doors: double-skin insulated metal doors with the required fire resistance, large enough to pass equipment, plus sanitary, staff, and office doors in accordance with the Internal Finish Schedule.

- Internal doors shall be considered as specified in the Internal Finish Schedule.

- Floor finishes: epoxy screed (minimum 5 mm thick) with epoxy seal coat for all electrical rooms without a raised floor, including the store room and corridor; parquet flooring for the office; acid-resistant ceramic tiles for the battery and charger room; and ceramic tiles for sanitary facilities and kitchen.

- Internal walls: brickwork, plastered, emulsion paint.

- Exterior walls: cavity masonry or double-twin wall with thermal insulation; plastered and painted inside; rendered and weatherproof painted outside.

- Windows: the building shall receive aluminum-framed windows with double glazing to provide natural light in the rooms.

- Access: for access into the building, a concrete platform with two steps or ramps shall be provided in front of the building. For access to the roof, an external steel service ladder with a safety cage after 2.20 m shall be provided.

- Heating: electric system.

- Air conditioning: split units (central system also possible, subject to Employer approval).

- Ventilation: provided in the switchgear and battery charger rooms, sanitary rooms, and kitchen.

- Sanitary equipment: toilet rooms with wash basins, western-type WC, urinals, shower tray, etc.

- Furniture: including two desks, two office tables, four swivel chairs, two visitors' chairs, and two cupboards for each of the office room and control room. All other rooms shall be provided with adequate furniture as approved by the Employer.

- The SCADA, RTU, and Telecommunication rooms can be provided in one large room.

### Internal Finish Schedule — Flooring, Walls, Ceiling, Doors and Windows

| Location | Flooring & Skirting (150 mm high) | Wall Internal | Ceiling | Doors, Windows, Ventilators |
| --- | --- | --- | --- | --- |
| Control Room | Vitrified tiles, 8 mm thick, 600×600 mm | Oil-bound washable distemper on smooth surface with 2 mm POP putty | RCC ceiling, white wash, and false ceiling | Anodized aluminum sections; flat drawn sheet glass, min. 5.5 mm thick |
| Offices, Conference, Corridor, Staff, Lab rooms | As Control Room | Oil-bound washable distemper with POP putty | RCC ceiling, white wash, false ceiling | Aluminum doors/windows with 5.5 mm glazing |
| Reception / Lobby | Vitrified tiles, 8 mm, 600×600 mm | Oil-bound washable distemper with POP putty | RCC ceiling, white wash, false ceiling | Anodized aluminum, 5.5 mm glazing |
| Battery room | IPS flooring | Dry distemper | White wash | Steel door 45 mm thick, double sheet 18G steel, mineral wool fill; aluminum windows/ventilators, 5.5 mm glazing |
| DCDB, MCC Room | Concrete flooring | Dry distemper | White wash | Steel double-sheet door; aluminum windows/ventilators, 5.5 mm glazing |
| Toilet, Pantry, Janitor's room | Vitrified tiles, 8 mm, 600×600 mm | Dado glazed tile up to RCC slab | White wash | Aluminum-framed particle-board door; aluminum windows/ventilators, 5.5 mm glazing |
| Switchgear Room | Concrete flooring | Oil-bound washable distemper, 2 mm POP putty | White wash | Anodized aluminum sections; flat drawn glass, min. 5.5 mm |
| Store building | Concrete flooring | Dry distemper | White wash | Rolling shutter and steel double-sheet door; hot-rolled steel framed glazed windows and ventilators with steel grill, 4 mm glazing |

Walls

Control room buildings at Qush Tepa and Darzaab shall be of RCC-framed structure. All walls shall be non-load-bearing walls. Minimum thickness of external walls shall be 350 mm brick masonry with 1:3 cement-sand mortar.

Plastering

All internal walls shall have a minimum wall thickness of 230 mm, with 15 mm thick plaster on the smooth side and 15 mm thick plaster on the rough side of the brick wall using cement mortar 1:3, and the ceiling shall have 10 mm thick 1:3 cement-sand plaster.

External Finishing

External plaster, 18 mm thick, shall be of 1:3 cement-sand plaster applied in two layers: an under-layer 12 mm thick and an upper layer 6 mm thick. The external surface of the building shall be painted with an approved acrylic smooth exterior paint of equivalent quality, resistant to the climatic conditions of Jawzjan Province.

Roof

A sloping RCC cast-in-situ roof shall be provided for all buildings, with a 10 mm gypsum false ceiling as mentioned in the finish schedule; the store room may be provided without a false ceiling.

False Ceiling

The control room and all other areas specified in the internal finish schedule shall have a closed aluminum ceiling system comprising 84 mm wide, 12.5 mm deep panels of approved color with a recessed flange of 23.9 mm, roll-formed from 0.5 mm thick aluminum alloy AA 5050/5052/3003, achromatized and stove-enameled on both sides. Panels shall be fixed on roll-formed carriers 32 mm wide, 39 mm deep, of minimum 0.9 mm thick aluminum alloy strip, in a module of 100 mm minimum at maximum 1.6 m centres, suspended from the roof by 4 mm diameter galvanized steel wire rod hangers with height-adjustment spring clips at maximum 1.5 m spacing. The system is to be approved by the Employer/Engineer-in-Charge before installation.

Doors and Windows

The details of doors and windows of the control room building at each site shall be as per the Internal Finish Schedule and relevant code. Rolling steel shutters and rolling steel grills shall be provided as per layout and requirement of the buildings. Paints used shall be of best quality specified as per relevant Afghanistan codes.

Partition

Partitions made of anodized aluminum frames provided with 5.5 mm thick clear glass shall be supplied and installed between the relay area and the control room at each site. The proposed arrangement of the buildings can be modified by the Contractor according to specific conditions, subject to the Employer's/Engineer's approval.

### 3.3  Gatehouse

- The Gatehouse at each of the Qush Tepa and Darzaab substations shall be a single-story reinforced concrete roofing with brick masonry wall structure, located at or near the main entrance. It shall serve as the primary point of access control, visitor registration, and security monitoring for the facility.

- The design, layout, and facilities of the Gatehouse shall ensure the safe and efficient control of personnel and vehicular access while maintaining the highest standards of operational security.

- The Gatehouse shall be located adjacent to the main entrance gate, allowing clear visibility of all incoming and outgoing traffic, with its orientation providing an unobstructed view of access roads and entry points.

Facilities to be provided in the Gatehouse shall include, but not necessarily be limited to, the following:

- Security desk and workspace for security personnel

- Waiting area for visitors

- Restroom (toilet and handwashing basin)

- Storage space for security and administrative equipment

- Electrical distribution panel for local services

- Communication and alarm systems (telephone, intercom, CCTV monitoring screens, access control systems)

- Doors and Windows: external doors shall be steel security doors with locking mechanisms; internal doors shall be high-quality aluminum.

- Windows shall be secured with reinforced glass and fitted with security grilles if required.

- HVAC: adequate heating, ventilation, and air conditioning shall be provided for occupant comfort. If additional rooms are deemed necessary as per project requirements at either site, the Contractor shall be obligated to incorporate them during the design phase without any additional cost.

### 3.4  Warehouse Building

The warehouse building at each of the Qush Tepa and Darzaab substations will also be designed by the Contractor, having at least a surface area of 240 m² (or 20.00 × 12.00 m). An eventual other division of the warehouse room can be indicated during the design of the building by the Contractor and approved by the Employer.

General Description

The Warehouse Building shall be a single-story, durable, reinforced-concrete-framed structure (including 30 MPa RCC foundation, columns, slab, and beam plus truss, and brick masonry walls or insulated sandwich panels) designed to provide secure, ventilated, and organized storage space. It shall be located within the substation perimeter fence, with easy access for authorized personnel and delivery vehicles. The design shall ensure protection against environmental conditions such as dust, moisture, and temperature variations typical of Jawzjan Province.

Location and Access

- The Warehouse shall be located conveniently for vehicle access while maintaining necessary clearances from energized equipment.

- Adequate paved access roads and maneuvering space for loading/unloading shall be provided.

- Loading/unloading area with heavy-duty door(s)

- Adequate lighting, ventilation, and security systems

- Fire safety equipment (fire extinguishers, alarms, etc.)

Construction and Finishes

- Structure: reinforced concrete framed structure with masonry walls or insulated sandwich panels.

- Flooring: reinforced concrete floor with a heavy-duty, dust-proof, and oil-resistant finish.

- Walls: durable internal and external wall finishes resistant to moisture, heat, and dust.

- Roofing: insulated, waterproof roofing system (truss) with appropriate rainwater drainage provisions.

- Doors and windows: industrial-grade, heavy-duty steel roller shutter or sectional doors for loading bays; personnel access doors with secure locks; windows (if provided) fitted with security grilles and insect screens.

Environmental Control and Electrical Installations

- Mechanical ventilation shall be provided to control humidity and temperature levels within acceptable limits.

- Where necessary, provisions for HVAC systems shall be included to protect sensitive materials.

- Internal lighting suitable for warehouse operations (LED or equivalent high-efficiency fixtures).

- External security lighting around the building perimeter.

- Sufficient general-purpose electrical outlets for equipment use.

- Lightning protection system integrated with the substation's earthing system.

Security Features

- CCTV surveillance cameras covering entrance points and interior spaces.

- Alarm system integrated with the substation's overall security network.

### 3.5  Outdoor Foundations

Transformer Foundations — General Requirements

The foundation supporting each power transformer at the Qush Tepa and Darzaab substations shall incorporate transformer transport rails. Bollards to give haulage points for the transformers shall be provided at suitable locations.

Provision shall be made for the catchment of oil spillage, rain, and fire-extinguishing water. Appropriate measures shall be taken to prevent pollution of the environment by discharge of ejected oil. Each transformer foundation tray shall be provided with a slope and raised borders, enclosing an oil pit in which the oil content of one transformer can be discharged in the event of an oil leak.

Each transformer compound shall be designed to retain 1.25 times its oil volume by means of oil-retaining walls in the event of failure or spillage, with provision for catchment and drainage to an underground oil sump tank and subsequent removal of the oil.

The transformer compounds shall be of sufficient size to permit safe working and provide adequate space for installation, maintenance, removal, and cooling of the transformers.

The oil pits inside the transformer foundation compound shall drain into one central underground oil-collecting pit with an integrated oil separator.

The area within the transformer enclosure shall be designed as a water-retaining structure to BS 8007 (or equivalent), and all internal concrete surfaces of the transformer trays likely to contact oil shall be painted with oil-resistant paint. The area within the transformer enclosure shall be coated with 2 coats of bituminous paint and surfaced with a 100 mm thick layer of gravel on steel grating.

Design Criteria

- The foundation design shall comply with the manufacturer's loading specifications and local geotechnical conditions at each site.

- Minimum thickness, reinforcement detailing, and concrete grade shall follow applicable standards such as ACI, Eurocode, or equivalent international codes.

- The finished level of the transformer pad shall be above the surrounding ground level to prevent water ingress.

- The road immediately adjacent to the transformer used by oil-handling equipment for maintenance shall also drain to the containment facility to prevent ground pollution in the event of accidental spillage.

- Where more than one power transformer exists on a site, it may be economical to link the oil-containment drainage areas to a single underground tank sized for the largest transformer alone, reducing the excavation required.

- Connection pipework shall be designed to ensure rapid discharge of oil to the underground facility and shall be resistant to transformer oil at temperatures up to 80°C.

Oil Drainage and Separation System

- An impervious oil collection pit shall be constructed beneath each transformer to collect any oil leakage or spillage.

- The pit shall be connected to an underground drainage system capable of channeling spilled oil and rainwater runoff away from the transformer area.

- A dedicated oil/water separation unit shall be installed to treat the collected fluids before discharge.

- The separator shall be designed to meet local environmental and discharge regulations and shall have sufficient capacity to handle the worst-case spillage scenario combined with rainfall events.

- Manual or automatic shutoff mechanisms shall be provided to prevent oil from escaping into stormwater drains.

- The oil-collecting pit shall be sized to accommodate at least 150% of the oil volume of the transformer, to allow for firefighting materials applied externally by the firefighting services.

Firewall for Transformer Protection

The firewall for transformer protection at each substation shall be constructed in accordance with IEC 61936-1 and NFPA 850 standards, designed to resist and contain fire, heat, and blast effects in case of transformer failure. The wall shall be made of reinforced concrete with a minimum thickness of 250 mm and a minimum fire-resistance rating of 3 hours (REI 180), capable of withstanding temperatures exceeding 1000°C. The height of the firewall shall be at least 1 m above the top of the transformer and extend 1 m beyond the width of the transformer on both sides. Foundations must be designed to accommodate the wall's weight and withstand seismic and wind loads per local or international codes. The firewall shall be located at a minimum horizontal distance of 1.5 m from the transformer, ensuring sufficient clearance for ventilation and maintenance.

Reinforcement shall be designed according to ACI 318 or an equivalent standard, with adequate cover to resist fire exposure. The surface shall be smooth and sealed to prevent oil penetration. Openings are not permitted in the firewall unless protected with certified fire-rated assemblies. Steel components such as embedded plates shall be protected with intumescent paint. All joints and penetrations shall be sealed with fire-stopping materials. Earthing shall be integrated to prevent potential rise in case of faults. The construction shall be inspected and approved by the responsible engineer, with quality-control test records for concrete strength and fireproofing materials maintained for both substation sites.

Outdoor Foundations — General

The following foundations are included, but are not limited to, the types listed below, at both the Qush Tepa and Darzaab substations:

- Foundations for outdoor switchgear equipment, supports, gantries, and foundations for BMK, lightning arresters, and poles, etc.

- Cable ducts, reinforced concrete trenches, and ducts

Special attention and security measures have to be taken in any extension areas where part of the installation is under operation. Existing disturbed roads and surfaces damaged during the execution works will be repaired by the Contractor to the full satisfaction of the Employer.

The overload factors for the stability of the foundations (overturning, sliding, bearing, and uplift) shall be at least 2.5 for normal loading conditions and at least 1.5 for exceptional loads.

The foundations shall be performed according to the requirements of the site-specific soil investigation. Soil conditions met during the foundation works shall be checked by the Contractor's soil engineer, recorded, and compared with previous results. If essential differences occur, the Contractor has to inform the Employer/Engineer and propose further measures. Immediately prior to concreting, the Contractor has to verify the specified soil conditions below the foundation level by a sounding method.

### 3.6  Roads, Paving and Surfacing

The road system at each substation must be arranged in such a way that non-obstructed traffic is guaranteed.

- The main road (from the entrance gate to the switchyard), the road all around the switchyard, and access roads shall be minimum 6 m wide; only the inside switchyard roads may be 5 m wide with 1 m shoulders. The minimum radius of main roads has to be designed for heavy vehicles and trailers.

- Main road connections to the buildings are to be provided by the Contractor, even if not shown on the general layout drawing. The access road connections from public roads to each site, and the main station roads, are part of the scope of civil works.

- The access road at each site shall be an asphalt road, extending from the nearest public highway to the respective substation switchyard area, with a width of 6 m.

- The roads shall be provided with slopes not exceeding 5%, if necessary.

- Footpaths of 1.0 m width shall be provided around the control/switchgear building at each site. Areas around the buildings and outdoor areas that can be used infrequently as lay-down areas for small loads, parking, etc., shall be paved with interlocking concrete blocks.

- The area of each switchyard not covered by buildings, foundations, structures, roads, paving, plants, etc. shall be leveled and covered by a gravel surface of minimum 15 cm thickness.

- Road signs, traffic signs, and road surface marking shall be provided as per the authority's requirements for traffic in industrial areas.

- The roads and paving shall be provided with slopes to lead the stormwater to side ditches and to the discharge system.

The Employer's instructions regarding the addition of water to improve compaction of fill must be adhered to. For filling under roads and foundations, every effort shall be made to compact the fill material at its optimum moisture content. In any case, the dry density of the compacted soil shall not be less than 98% of the maximum density according to AASHTO T180.

The complete substation area at each site shall be surfaced with a 150 mm layer of crushed aggregate, size 32–64 mm.

For the materials, construction, and quality requirements for the binder course and wearing course of asphalt pavement for roads within and leading to each substation, all works shall conform to AASHTO specifications and good engineering practice.

The flexible pavement shall consist of the following asphaltic concrete layers:

- Wearing Course: minimum compacted thickness of 40 mm.

- Binder Course: minimum compacted thickness of 60 mm.

Binder course: the asphalt mix shall conform to AASHTO Hot Mix Asphalt (HMA) design using the Marshall Method. Wearing course: the wearing course shall use a finer gradation asphalt mix, incorporating anti-stripping agents if required.

For dimensioning the roads at Qush Tepa and Darzaab, actual heavy traffic loads will have to be considered; however, as a minimum, the specific standard load of truck SLW 60 (according to ISO TR 9492 or equivalent standard) shall be considered for the dimensioning of roads.

Sub-Base

Sub-base material shall be crushed rock or other approved local material having suitable properties and conforming to the following grading:

| BS Sieve | Percentage by Weight |
| --- | --- |
| 75 | 100 |
| 37.5 | 85–100 |
| 10 | 45–100 |
| 5 | 25–85 |
| 0.6 | 8–45 |
| 0.075 | 0–10 |

The sub-base shall be compacted by approved plant to a dry density not less than 98% relative compaction until movement of the surface ceases and the surface is closed.

Wet Mix Road Base

Wet Mix Road Base material shall consist of crushed gravel or crushed rock, suitably proportioned to conform to the following grading, as approved by the Employer/Employer's Representative:

| BS Sieve | Percentage by Weight |
| --- | --- |
| 50 | 100 |
| 37.5 | 90–100 |
| 20 | 60–80 |
| 10 | 40–60 |
| 5.00 | 25–40 |
| 2.36 | 15–30 |
| 0.600 | 8–22 |
| 0.075 | 0–8 |

Material constituents shall comply with the following maximum limits — for material passing the 0.425 mm sieve: liquid limit 25%, linear shrinkage 3%, plasticity index 6%. For coarse material: stone size aggregate 50 mm, aggregate crushing value 25%, water absorption 2%, flakiness index 35%, elongation index 35%.

The base shall be compacted by approved plant to a dry density not less than 98% relative compaction. The final surface shall be shaped and finished true to line and level within a tolerance of ±10 mm to the levels shown on the drawings.

Placing of Road Base

Wet mix road base material shall be crushed and mixed by an approved mechanical placing plant. Water for adjusting the moisture content shall be added to the mixer; if required, the moisture content shall be adjusted to allow for evaporation of road base moisture during transportation. After mixing, the material shall be removed from the mixer and transported to the placing location without delay.

The compaction procedure and plant shall be proved by trials at the commencement of the works at each site. The road base shall achieve a minimum dry density of 98% of the maximum laboratory dry density and an in-situ CBR (per BS 1377) value of not less than 80%, or modified Proctor density of 97% according to DIN 18127.

Hard Shoulders and Bitumen Macadam

The material used for any hard shoulders shall comply with the General/Particular Technical Requirements for wet-mix road base.

Aggregate for bitumen macadam shall be hard, clean, durable crushed rock or gravel, and sand, all in accordance with approved standards, obtained from an approved source. Coarse aggregate is defined as that fraction retained on a 3.5 mm BS sieve, with physical properties not exceeding: aggregate crushing value 20% (wearing)/25% (base), flakiness index 25%/30%, elongation index 25%/30%, water absorption 2%/2%. The wearing course shall be of 40 mm finished thickness. Bitumen shall be of Grade 60/70 penetration.

Interlocking Paving Blocks

Roads and areas to be paved with interlocking concrete blocks shall be excavated and placed with a 300 mm depth of compacted material at the exact levels and falls required for the finished work. If parts of the base are found to be unstable, the Contractor shall excavate further to a firm bed and fill with layers of fine crushed rock or aggregate, thoroughly compacted.

A stable edge shall be provided to retain the paving units and sand bedding by means of a precast concrete edging unit or curbs set in situ concrete. The sand bedding shall be a fine, well-graded sand in a dry-to-moist condition, laid to an un-compacted thickness of 50 mm. The interlocking block shall be a minimum of 80 mm thick, and concrete quality must be approved by the Employer/Employer's Representative.

Road Marking

Thermoplastic paint is preferred for its durability; alternatively, pre-formed tapes or solvent-based paint may be used with prior approval. Paint shall be lead-free, fast-drying, and weather-resistant. Glass beads (Type I or II) shall be applied to enhance reflectivity (per AASHTO M 247). All road marking works shall comply with AASHTO M 249, ASTM D713, MUTCD, and local traffic engineering standards, where applicable. Markings shall have a minimum lifespan of 12 months without significant fading or damage.

Road Geometry

| Parameter | Requirement |
| --- | --- |
| Access and Main Road Width | 6.0 m (main roads) |
| Shoulders | 1.0 m each side |
| Minimum Horizontal Radius | 16 m (at low-speed zones) |
| Maximum Gradient | 4% (unless otherwise specified) |
| Cross Slope (Camber) | 2% for asphalt; 3–4% for gravel roads |
| Turning Radius at Gates and Corners | Sufficient for a 12 m trailer turning (≥16 m) |

Drainage and stormwater management: all roads shall have adequate side drains, culverts, and slope protection, with a minimum longitudinal slope of 0.5%. Roadside ditches shall be lined with reinforced concrete.

### 3.7  Boundary Wall

General Requirements

- The whole of each substation (Qush Tepa and Darzaab) shall be surrounded by a stone masonry and brick wall, including Y-shaped posts plus concertina wire with all related accessories.

- Wall height: minimum 3 m above ground level, plus 0.6 m of concertina wire (total 3.6 m).

- Thickness of the brick wall above the stone masonry: minimum 350 mm; stone masonry below the brick wall: minimum 600 mm.

- Foundation depth and width shall be designed based on the site-specific soil investigation report/site soil conditions.

- Construction joints: provided at every 15 m and at wall corners.

- Coping: PCC coping with slope to prevent water ingress.

- An RCC ring beam at the top of the stone masonry shall be considered, with a cross section of (350×350) mm.

Materials for Stone Masonry Wall Foundation

- Stone type: locally available hard, durable stone, free from cracks and weathering.

- Mortar: cement-sand mix (1:4), mechanically mixed, with proper workability.

- Joint thickness: not exceeding 15 mm; joints raked to receive plaster.

Materials for Brick Masonry Wall

- Brick type: first-class, well-burnt clay bricks, conforming to ASTM C62 or equivalent.

- Strength: compressive strength ≥ 10 MPa.

- Mortar: cement-sand mix (1:4).

- Plaster: 12–15 mm cement-sand plaster (1:4), both sides, unless an exposed finish is approved.

Coping and Security Features

- Coping: cast-in-situ RCC coping slab, 75–100 mm thick, weathered top.

- Gate pillars: reinforced concrete piers with embedded holdfasts for gate installation.

Solid Sliding Gate — General Requirements

- The sliding gate at each substation entrance shall be designed for the perimeter security of a 220/20 kV substation.

- It shall be robust, weather-resistant, and capable of withstanding high wind loads and mechanical impacts.

- The gate shall operate smoothly, either manually or automatically, with minimal maintenance.

Gate Type and Dimensions

- Type: horizontal sliding gate; Operation: motorized with manual override; Design: single leaf, cantilever, or bottom-track type depending on site conditions.

- Clear opening width: minimum 6.0 m or customizable as per access road width.

- Height: 3 m above ground level.

- Gate length: overall length to include counterweight section (typically 1.5× clear opening).

- Track: galvanized steel track with suitable drainage.

Materials, Coating, and Drive System

- Frame: hot-dip galvanized steel rectangular hollow sections (RHS) or equivalent — minimum 70×70×4 mm.

- Top and bottom rails: reinforced RHS or I-beam section to resist deflection.

- Rollers (for bottom-track): heavy-duty polyurethane or steel with sealed bearings.

- Cantilever supports (if used): heavy-duty galvanized steel posts with roller support arms.

- All steel components shall be hot-dip galvanized per ASTM A123 (or equivalent) and powder-coated (polyester or epoxy) as per client requirement, with corrosion protection ensuring a minimum service life of 25 years in outdoor conditions.

- Motor: 230V or 400V AC motor (3-phase preferred), IP65 rated. Control panel: weatherproof enclosure with start/stop buttons, emergency stop, and manual override. Drive mechanism: rack-and-pinion or chain drive with limit switches. Operating speed: 10–15 m/minute (adjustable). Remote operation: optional, via remote control or integrated with substation access control system.

Foundation and Civil Works for the Gate

- Reinforced concrete footing for track or cantilever post supports, designed based on local soil conditions, with a minimum concrete compressive strength of 30 MPa.

- Reinforced concrete column and foundation for the personnel gate and solid sliding gate.

- Ground level to be kept flush with track (if applicable) with drainage provided to avoid water accumulation.

Personnel Gate

- The personnel entry gate at each substation shall be designed for secure pedestrian access.

- It shall provide durability, weather resistance, and ease of operation.

- The gate shall be coordinated with the perimeter wall and the main sliding gate in both function and appearance.

- Type: single-leaf swing gate; Operation: manual with heavy-duty lock mechanism; Swing direction: outward-opening or inward-opening based on site layout and evacuation requirements.

- Clear width: 1.2 m (typical for single pedestrian access). Height: 3 m (matching the perimeter wall height). Clearance: minimum ground clearance of 50 mm for smooth operation.

Standards and Codes

- IEC 62271-1 for substation safety.

- ASTM A123 for galvanizing.

- ISO 1461 for hot-dip galvanized coatings.

- Local building and electrical codes.

Concertina Wire (Ø 600 mm) on Top of Brick Wall

The concertina wire shall provide an additional layer of physical security on top of each substation's perimeter brick wall cap. It shall be high-strength, corrosion-resistant, and installed to effectively deter unauthorized access.

- Type: galvanized steel razor-type concertina coil. Coil diameter: 600 mm (expanded). Loop overlap: 45–50% overlap to prevent opening between loops.

- Core wire: high-carbon spring steel, diameter 2.5 mm (±0.1 mm), tensile strength ≥ 1200 MPa, coating electro-galvanized or hot-dip galvanized (minimum 80 g/m²).

- Razor tape: cold-rolled galvanized steel, thickness 0.5 mm (±0.05 mm), width 19 mm (±1 mm), barb length 13–15 mm, barb spacing approx. 26 mm.

- Support brackets: hot-dip galvanized steel angle or flat bar, Y-type, height above wall minimum 600 mm, fixed into the top of the brick wall at 2.0–2.5 m intervals or at steel posts.

- Fixing method: minimum 3-point fixing per bracket to ensure tautness and prevent sagging; stainless steel or galvanized tie wire (2–3 mm).

- All components must be galvanized or stainless steel, conforming to ASTM A123/ISO 1461 or equivalent, with an expected lifespan of ≥ 10 years under outdoor exposure.

### 3.8  Chain Link Fences and Gates

The Contractor shall provide external fencing according to the requirements at both the Qush Tepa and Darzaab substations. In areas where the security of the equipment requires internal fences, these shall also be provided.

The Contractor shall design, furnish, and install a chain link fence and gates around the whole switchyard of each substation area, and all parts of the fence shall be corrosion-resistant, galvanized.

The fence shall be designed to withstand environmental exposure, mechanical damage, and minor impacts. Each wire shall have a minimum failure load of 2,000 N. Straight-line posts shall have a minimum bending failure load, applied horizontally on top in the most unfavorable direction, of 600 N. Top and bottom tension wires shall have a minimum failure load of 5,000 N. In case of a 2 m or higher chain link, the top wire shall be substituted by a top rail. Barbed wires shall have a minimum failure load of 3,000 N.

The fence shall be connected to the earthing system to prevent dangerous touch voltages. The total height of the fence above the ground shall be at least 2.00 m.

The tension wire shall be made of plastic-coated galvanized steel, erected 0.20 m above the top of the perimeter RCC beam and at the midpoint of the fence. The perimeter RCC beam shall be made of reinforced concrete with a size of 200×300 mm.

Fence Posts

- Line posts: 65 mm OD steel pipe (3–4 mm thickness) — spaced at 2.5–3.0 m intervals.

- Corner posts: 75 mm OD steel pipe (4–5 mm thickness) — with bracing.

- Gate and end posts: 75–100 mm OD pipe or equivalent.

- Height: minimum 2.0 m. Coating: hot-dip galvanized (minimum 80 µm), conforming to ASTM A123 or ISO 1461.

Chain Link Fabric

- Material: galvanized steel wire. Mesh size: 50 mm × 50 mm (diamond mesh). Wire diameter: minimum 4 mm (8 SWG) before galvanizing.

- Coating: hot-dip galvanized, minimum 275 g/m² zinc coating (per ASTM A392 Class 2). Height of fabric: 2.0 m.

- Top and bottom edges: knuckled or twisted/barbed depending on the security requirement.

Post Foundations, Top Rail, and Accessories

- Concrete footing size for line posts: 400×400×700 mm depth (min.); for corner/end posts: 500×500×900 mm depth (min.); concrete grade C25 or higher, cured for at least 7 days before applying tension to the fabric.

- Top rail (optional): 32 mm diameter steel pipe for additional rigidity. Bracing: diagonal braces at corners and gate openings, securely fixed to posts and concrete.

- Tension wire (6 mm galvanized) for middle and bottom tying of the fabric; galvanized tension bands and clamps; hot-dip galvanized bolts, nuts, and washers; gate hinges and latches.

- All posts shall be set vertically and aligned both horizontally and vertically. Chain link fabric shall be stretched tight and tied to posts using binding wire at max. 30 cm intervals. All sharp edges, wire ends, and fasteners must be secured to prevent injury.

Standards and Codes

- ASTM A392 – Zinc-Coated Chain-Link Fence Fabric.

- ASTM A123/ISO 1461 – Hot-Dip Galvanized Coatings.

- IEC 62271-1 – General safety requirements for substations.

- Local codes and utility specifications for fencing and security.

Fence Gate — General Description

The fence gate at each substation shall be fabricated to match the adjoining chain link fence in terms of height, material, finish, and durability. It shall provide secure and controlled access for vehicles or personnel, with reliable locking and corrosion protection.

- Gate type: single-leaf for personal entry (1.2 m wide); double-leaf for vehicle access (typically 4–6 m clear opening); height 2 m (to match fence).

- Frame material: mild steel pipe or RHS — size 50×50×3 mm (personal gate); 75×50×3 mm or larger (vehicle gate).

- Infill: galvanized chain link mesh matching the fence — 50×50 mm mesh, 4 mm (12 SWG) wire, galvanized.

- Hinges: heavy-duty galvanized or stainless-steel hinges (3 or 4 per leaf). Locking system: padlock-compatible latch with hasp; optional mortise lock, electromagnetic lock, or keypad for personnel gates.

- Stopper: ground stopper or catch for vehicle gates to prevent swing-back. Drop bolt: galvanized steel drop bolt for securing double-leaf gates.

- All steel components shall be hot-dip galvanized (minimum 80 µm, per ASTM A123/ISO 1461).

- Gate posts: steel pipe or angle post, hot-dip galvanized. Personal gate: 75 mm OD × 4 mm thick pipe. Vehicle gate: 100 mm OD × 4.0 mm thick pipe or equivalent RHS.

- Foundation: concrete footing (min. 600×600×900 mm) using C25 concrete, with anchor bolts or embedded posts grouted with non-shrink grout.

### 3.9  Stormwater Drainage System

The stormwater drainage system at each substation shall collect only clean stormwater, discharged into the local stormwater system where available, or to an approved natural or engineered discharge point near Qush Tepa or Darzaab respectively. For each new substation, a complete stormwater drainage system is required. Substantially maintenance-free and operationally safe installation must be guaranteed. Surface water drainage shall include all necessary gutters, downpipes, gullies, traps, catch pits, and manholes. Within each substation, only coordination of the new drainage with any existing local system needs to be realized. For more details, refer to Section 9.

### 3.10  Sanitary Sewage Drainage

The sanitary sewage drainage system at each substation shall cover all works and materials required for the collection, transportation, and safe disposal of domestic wastewater from the substation facilities. This includes internal and external piping, inspection chambers, septic tanks, soak pits, and other associated infrastructure.

The sanitary water from the WC, urinals, shower, wash basins, and kitchen shall be discharged to a three-chamber treatment plant made of reinforced concrete, at each site. The pre-cleaned water shall be led to a soak-away pit. For more details, refer to Section 7.

### 3.11  Landscaping

This specification covers the supply, preparation, planting, and maintenance of landscape areas within and around each substation compound (Qush Tepa and Darzaab), including green belts, lawn areas, trees, shrubs, and gravel zones for dust and erosion control.

The free area of land inside each substation, where no roads or gravel is provided, shall be landscaped using low-to-medium-high growing plants and grass suited to the semi-arid climate of Jawzjan Province. Plantations shall be provided along the main roads and the buildings. The landscaping is subject to the approval of the Employer/Engineer.

### 3.12  Retaining Wall Construction

The Contractor is responsible for the construction of stone masonry or RCC retaining walls in stepped, sloped, and flood-protection areas of the Qush Tepa and Darzaab 220/20 kV substation sites, where required. The retaining wall shall provide lateral support to the soil and protect the substation infrastructure from erosion, sliding, and flooding.

The minimum compressive strength of the stone shall not be less than 25 MPa (or as per design). The stone should be hard, durable, angular stone from approved quarry sources, free from weathering, cracks, organic matter, or other deleterious substances. Cement-sand mix ratio: 1:4 (1 part Portland cement to 4 parts sand) by volume; clean and potable water free from harmful impurities shall be used.

### 3.13  RCC-Framed Gatehouse with Steel Truss Roof

This specification outlines the technical requirements for the construction of a gatehouse building with an RCC-framed structure and a steel truss roof at the entrance of each of the Qush Tepa and Darzaab 220/20 kV substations. The structure shall accommodate security operations and control of substation access. A single-story RCC-framed structure with brick infill walls, plastered and painted, is required.

The Contractor is responsible for considering the toilet, waiting, and bed areas in the gatehouse, constructed as per standard requirements. RCC isolated/pad footing or combined footing shall be used, depending on soil-bearing capacity, with a minimum concrete compressive strength of 30 MPa.

### 3.14  RCC Framed Pump House

This specification covers the construction of a reinforced concrete (RCC) framed pump house, with masonry infill walls and sloped slab, suitable for accommodating one or more water pumps, associated piping, electrical panels, and maintenance access, at each of the Qush Tepa and Darzaab 220/20 kV substations.

### 3.15  RCC Framed Overhead Water Tank

The construction of the overhead water tank structures at both the Qush Tepa and Darzaab substations falls within the scope of the Contract. The Contractor shall be responsible for executing the works in full compliance with the project requirements and applicable standards.

## 4.0  General Design Requirements

### 4.1  Instructions for the Basic Design

- The civil works are governed by the conditions of the electromechanical part and the conditions or specifications stipulated hereafter, applicable equally to the Qush Tepa and Darzaab substations.

- This document represents the basic specification information for calculating the lump-sum price of the works concerned but should not be considered a complete description in every respect. Bidding drawings indicate the intended layout of the works but are not to be taken as a final and dimensional reference.

- The price offered shall be understood as the total sum for the complete civil and finishing works to suit the requirements and functions of the works concerned, for both substations combined, unless priced separately in the Bill of Quantities.

- Design and choice of construction materials shall consider and ensure the reduction of future maintenance works; all civil elements shall be designed to minimize maintenance and to result in a durable construction with a minimum design life of 40 years.

- The Contractor shall prepare all necessary design and detail drawings in accordance with the project requirements, for each site.

- The design of all structures under this Contract shall be such that differential and total settlements or other movements shall not exceed acceptable limits, and full provision shall be made for all expansion and other joints. The design shall be subject to the approval of the Employer.

- Structural members subjected to flexure shall be designed to have adequate stiffness to limit deflections or any deformations that adversely affect the strength or serviceability of a structure. Maximum allowable deflections of structural members shall be in accordance with the relevant design standards and/or the limits prescribed by the machinery manufacturers.

- The dimensions of all buildings and structures shall provide adequate space for the safe installation and proper operation, maintenance, and repair of all plant and equipment.

- In order to save energy for air conditioning, adequate thermal insulation of buildings has to be provided. The general transmission coefficient, including walls, roof, floor, and doors, shall be K ≤ 0.7.

- Suitable access to the roofs of the buildings shall be provided for maintenance and repair of any installation.

- All rooms with fire hazards shall be provided with suitable emergency exits.

- Safe, convenient, and straightforward access and means are to be provided to take equipment in and out of all rooms.

- If culvert(s), tunnel(s), trenches, or any other underground services cross roads, these shall be designed as bridges for truck loading without affecting the underground structures.

- The Employer/Engineer must approve all civil designs and drawings before the start of manufacturing/construction, for each of Qush Tepa and Darzaab.

- Proper access roads shall be provided to bring in all the equipment and take it out in case of maintenance. These access roads shall be suitable for the vehicles used (cars, forklifts, trucks/trailers, etc.) to reach the point of unloading of the equipment.

- Safe, convenient, and straightforward access means are to be provided to take equipment in and out of all rooms, at all levels, using suitable stairwells and suitable electric hoists. The dimensions of rooms, stairwells, doors, etc., shall be designed to suit the transport concept mentioned above.

### 4.2  Particular Architectural Requirements

The external aspects and finishing of buildings at Qush Tepa and Darzaab will be made in harmonic combination of elevation types with the local conditions, subject to the approval of the Employer or the Employer's Representative.

### 4.3  Responsibilities of the Contractor

The Contractor shall be solely responsible in all respects for the suitability and stability of the buildings, structures, and foundations at both substation sites.

This specification defines the Contractor's duties and obligations in executing all civil, architectural, and infrastructure works for the Qush Tepa 220/20 kV substation and the Darzaab 220/20 kV substation, in accordance with the approved design, drawings, specifications, codes, and project schedule.

General Responsibilities

- Execute the works in full compliance with drawings, technical specifications, contract terms, and applicable codes/standards.

- Coordinate with the Engineer-in-Charge and other contractors (e.g., electrical contractor) on both sites.

- Ensure the safety, quality, and timely completion of the works.

Site Preparation and Mobilization

- Mobilize construction equipment, manpower, and materials at both sites as per the agreed timeline.

- Conduct site cleaning, clearing, leveling, and layout marking at each site.

- Establish site offices, storage yards, material stockpiles, temporary fencing, and utilities (water/electricity) at own cost, at both sites.

Construction Activities

Perform all civil and structural works, including but not limited to the following, at each of the Qush Tepa and Darzaab substations:

- Foundations (equipment, gantries, buildings)

- Substation buildings (control room, battery room, stores, toilets, etc.)

- Cable trenches and ducts

- Roads and internal pathways

- Drainage systems (stormwater and sewage)

- Fencing, gates, and boundary wall

- Landscaping, backfilling, and site grading

- Gatehouse

- Pump house

- Warehouse building

- Provide formwork, reinforcement, concrete, and all construction materials.

- Ensure all work is executed in line with the approved method statements and inspection/testing plans.

Quality Assurance and Testing

- Establish a quality control plan and submit it for approval, covering both substation sites.

- Provide and operate on-site testing arrangements or coordinate with approved laboratories.

- Perform tests on construction materials (cement, aggregates, steel, etc.), concrete strength, compaction, and other required parameters.

- Maintain records of tests, inspections, and approvals for each site.

Health, Safety, and Environmental Compliance

- Implement a Health, Safety & Environment (HSE) plan approved by the Employer for both sites.

- Provide personal protective equipment (PPE) to all workers and staff.

- Ensure safe working practices and comply with all statutory safety regulations.

- Prevent pollution, manage construction waste, and control dust and noise levels.

Manpower and Supervision

- Deploy qualified engineers, supervisors, and skilled labor at each site, as per the manpower schedule.

- Maintain a site manager or resident engineer at each of Qush Tepa and Darzaab, who is the point of contact for site activities.

- Provide regular progress reports, site meeting participation, and documentation.

Drawings and Documentation

- Verify all drawings on-site and report any discrepancies.

- Maintain a copy of the latest approved drawings and specifications on-site, at both locations.

- Submit shop drawings, bar bending schedules (BBS), as-built drawings, and material submittals.

Keep daily logs, concrete pour records, and work progress registers for each site.

Protection and Maintenance of Works

- Protect all completed works from damage until final handover.

- Secure open excavations, trenches, or hazardous areas with barricading and signage.

- Carry out minor maintenance and rectification during the Defects Liability Period (DLP).

Coordination and Support

- Coordinate with utility providers and local authorities in Jawzjan Province for permits, inspections, or temporary services.

- Provide support to the Employer during inspections by third parties, consultants, or statutory bodies.

- Avoid disruption to ongoing electrical works or operational equipment.

Project Completion and Handover

- Ensure final cleaning, site clearing, and disposal of waste/debris at both sites.

- Carry out all punch list items prior to handover.

- Submit completion documents, including as-built drawings, test reports, warranties, and material certificates, for each substation.

- Conduct joint inspections and obtain completion certificates from the Employer for each of Qush Tepa and Darzaab.

Liability and Defect Correction

- Rectify defects identified during execution and within the Defect Liability Period (typically 12 months).

- Replace faulty materials or workmanship without extra cost.

- Maintain warranties on materials, components, and workmanship as per contract.

Final Acceptance

- The work at each substation will be accepted only after satisfactory completion, inspection, testing, and approval by the Employer/Engineer.

- Any outstanding issues must be resolved before the issuance of the final completion certificate.

### 4.4  Codes and Standards

The civil/architectural works for buildings and structures at Qush Tepa and Darzaab shall be designed and constructed according to the highest quality codes/standards specified and good engineering practice. All relevant laws, directives, codes, regulations, and ordinances must be complied with, in the latest version in each case. In particular, these include (the list is not exhaustive):

- EN standards/guidelines

- ACI 318 – Building Code Requirements for Structural Concrete

- ACI 301 – Specifications for Structural Concrete

- AISC 360 – Specification for Structural Steel Buildings

- ASTM A36 / ASTM A992 – Standard specifications for structural steel

- ASTM A500 / A53 – Steel pipe and hollow sections

- IBC (International Building Code) – General structural design and safety

- ASCE 7 – Minimum Design Loads and Associated Criteria for Buildings and Other Structures

- Afghanistan Building Code (ABC)

- MEW Water Management Regulations

- Workplace ordinance/guidelines, VDE guidelines

- VGB directives

- Accident Prevention Regulations

- Other international standards that have the status of EN standards

- Conditions, requirements, and recommendations from the applicable permits/licenses issued for Qush Tepa and Darzaab districts

### 4.5  Design Loads

The following design loads shall be considered for the design of buildings and structures at both the Qush Tepa and Darzaab substations:

Dead Load

- Dead load is defined as the weight of all permanent construction, including walls, foundations, floors, roofs, ceilings, partitions, stairways, and fixed service equipment, calculated according to DIN 1055-1 or equivalent.

- For substations, this includes equipment, pipes and accessories, electrical and lighting conduits, switchgear, instrumentation, fireproofing, insulation, ladders, platforms, and other similar items.

- Equipment and piping should be considered filled by product load when calculating dead load. The weight of soil overburden shall be considered as dead load.

- Erection dead load is the weight of the equipment at the time of erection plus the weight of the footing, pedestal, and overburden soil.

Live Load

- Live load is defined as the weight superimposed by the use and occupancy of the building or other structure, but not permanently attached to it; for industrial design, live load can be defined as the load produced by personnel, movable equipment, tools, and other items placed on the structure but not permanently attached.

- Crane loads shall be considered as live loads. Unless specified otherwise, the minimum live load values from the relevant design standard shall be considered; the Engineer's consent is required for any reduction of load-carrying capacities.

- Truck loads according to DIN 1072 or equivalent. Areas designated for different loadings on the same floor shall be clearly and permanently marked.

Thermal, Truck, Soil, and Hydrostatic Loads

- Thermal loads shall be defined as forces caused by changes in temperature, arising from expansion or contraction of vessels, piping, or the entire structure or individual structural components.

- Structures accessible to trucks shall be designed to withstand the gravity, lateral, and impact effects of truck loading. Truck loading shall be SLW 60 as defined by DIN 1072 (or equivalent).

- Soil loads shall consist of lateral earth pressures. Active and passive coefficients for lateral pressures shall be obtained from the site-specific project soils report for Qush Tepa or Darzaab. The weight of soil shall be considered as dead load.

- Hydrostatic load is the load due to water pressure. The design of structures shall include hydrostatic loads when applicable. The buoyancy load is equal to the weight of the volume of displaced water.

Wind, Snow, and Seismic Load

- The actual wind load for the calculation of buildings and structures shall be taken from local/national Afghanistan codes applicable to Jawzjan Province, or equivalent recognized codes where local data is unavailable, considering wind zone, wind speed, and snow load zone specific to the Qush Tepa/Darzaab climatic region.

- The seismic calculations of buildings and structures shall be prepared in accordance with the requirements of the relevant applicable standards, using data for the location of each project site. If no local standards are available, the provisions of the Uniform Building Code (or equivalent international seismic code) shall be applied.

Dynamic and Impact Loads

- Each structure shall be designed to withstand the effects of vibration and impact to which it may be subjected. Each structure and foundation supporting machinery having a significant dynamic unbalance shall be designed to resist the peak loads specified by the manufacturer.

The following impact loads shall be considered:

- Shaft or motor-driven machinery: 20% of machinery weight

- Reciprocating machinery: 50% of machinery weight

- Overhead travelling crane — vertical force: 25% of maximum wheel loads for cabin-operated cranes; 10% for pendant-operated cranes

- Lateral force: 20% of the weight of the trolley and the lifted load; longitudinal force: 10% of the maximum wheel loads

- Truck loads — vertical force: 20% of lifted loads

### 4.6  Foundation Design

This specification outlines the requirements for the analysis, design, detailing, and construction of reinforced concrete foundations for all civil and structural components of both the Qush Tepa 220/20 kV substation and the Darzaab 220/20 kV substation. The design shall conform to ACI 318 (latest edition) or equivalent applicable international standards for structural concrete and geotechnical design.

The foundations shall serve to support all loads from the equipment, buildings, and associated facilities. For the existing subsoil conditions at each site, the appropriate foundation types (isolated pad footings, combined footings, raft/mat foundations, or piled foundations, as determined by the site-specific geotechnical investigation) shall be applied to the buildings and structures of each substation.

### 4.6 Foundation Types

The following foundation types may be used at the Qush Tepa and Darzaab Substation sites, depending on the results of the site-specific soil investigation and structural requirements:

- Isolated spread footings (equipment support structures, transformers, etc.)

- Combined footings or mat foundations (in congested equipment zones)

- Pedestals with reinforced plinths (transformer foundations)

- Pile foundations (only where soil conditions require deep foundations)

End bearing piles, i.e., bored piles down into a deep stratum, shall be used for heavy constructions. Friction piles, i.e., driven piles, may be used for buildings where confirmed suitable by the geotechnical report.

Direct Foundations

- Direct foundations can be used when the allowable bearing capacity reaches values of approximately 1.0 – 2.5 kg/cm² under acceptable settlement conditions, as confirmed by the site-specific geotechnical investigation.

### 4.7 Design Criteria

Structural Design

- Foundations shall be designed using the limit state method per ACI 318.

- All structural members shall have adequate strength, serviceability, and durability.

- The design shall consider:

- – Dead loads (equipment self-weight, structure weight)

- – Live loads (maintenance, personnel)

- – Seismic loads (as per ASCE 7 and IEEE 693, using seismic parameters derived for the Jawzjan Province project sites)

- – Wind and uplift forces (from substation gantries and structures)

- – Dynamic loads (e.g., short-circuit forces, transformer vibrations)

Soil Bearing Capacity

- Soil properties shall be derived from the geotechnical investigation report prepared for the Qush Tepa Substation site and the Darzaab Substation site respectively (see Section 13).

- The allowable bearing pressure and settlement criteria must be satisfied for each site independently.

- Minimum factor of safety for bearing capacity: ≥ 3.0.

Minimum Structural Requirements

- Concrete strength (f'c): 30 MPa (4,351 psi)

- Reinforcement: High-yield deformed bars conforming to ASTM A615 or equivalent

- Minimum footing thickness: not less than 400 mm (for isolated footings)

Settlement Tolerances

The following are the acceptable limits of settlement for foundations at both sites:

- Buildings/structures: total settlement 25 mm; differential settlement 10 to 20 mm

Stability of Foundations

Stability against overturning shall be 1.5 for erection conditions, 2.0 for normal operating load conditions, and 1.5 for cases of transient loads such as earthquake or wind.

Stability against Sliding

The minimum safety factor against sliding shall be 1.5. The coefficient of friction used in computing the safety factor against sliding for cast-in-place foundations shall be 0.50, unless specified otherwise in a detailed soil investigation. Passive earth pressure from backfill shall not be considered in computing these safety factors.

Stability against Flotation

All foundations subject to buoyant forces shall be designed to resist a uniformly distributed uplift equal to the full hydrostatic pressure. The minimum safety factor against flotation shall be 1.10, considering the highest anticipated groundwater level recorded at the Qush Tepa and Darzaab sites.

Increase in Allowable Bearing Pressures

Allowable bearing pressures under foundations shall be increased by one third for load cases considering extreme loads such as wind or seismic forces, either acting alone or combined with vertical loads.

### 4.8 Special Civil Design Requirements

Introduction

The civil works for both the Qush Tepa Substation and Darzaab Substation are governed by the conditions of the electromechanical part and the conditions and specifications stipulated hereafter.

Detailed execution features of the civil work are described in the relevant sections of the Specifications. This document represents the basic specification information for calculating the lump sum price of the works concerned but shall not be considered a complete description in every respect. Bidding drawings indicate the intended layout of the works but are not to be taken as a final and dimensional reference.

The price offered shall be understood as the total sum for the complete civil and finishing works to suit the requirements and functions of the works concerned at both the Qush Tepa and Darzaab sites.

Design and choice of construction materials shall consider and ensure the reduction of future maintenance works; all civil elements shall be designed to minimize maintenance and to result in a durable construction with a minimum design life of 40 years, suitable for the continental climate of Jawzjan Province (hot, dry summers and cold winters).

The Contractor shall prepare all necessary design and detail drawings in accordance with the Project requirements.

Design Guidelines — Buildings

- Foundations shall be designed according to the findings of the site-specific soil investigations and shall consider the requirements of the buildings. Total settlement shall not exceed 2 cm, and differential settlement must be smaller than 1 cm.

- Cable floors/channels and respective cable tunnels (ease of access) shall be considered under all rooms.

- Raised modular flooring shall at least be foreseen for containers and control rooms.

- Provisions for heating, cooling, and ventilation shall be made for every individual conditioned space, fully supported by design (demand, losses, and resulting facility capacity requirements) appropriate to the local climatic conditions.

- An adequate number of doors/emergency exits shall be provided to comply with means-of-egress requirements, together with sufficient loading spaces as per related fire-fighting code requirements.

- All cable trenches shall be executed with at least 1% slope towards drainage points or pump sumps, provided for each section or at least at both ends of the trench. A recessed/flush installation shall normally be foreseen for all wall cabinets and panels (fire hose reels, breathing apparatus, fire extinguishers, annunciator/repeater panels, CO2 shut-off units, alarm/detection equipment, etc.).

- External walls, roofs, aluminum or metal-clad walls and roofs, as well as all doors and windows of all containers and buildings, shall provide adequate thermal insulation and shall be approved by the Employer/Employer's Representative. The thermal transmission coefficient of walls, including all windows and doors, shall comply with applicable standards, taking into account the extreme summer/winter temperature range at both sites.

- Unless local regulation requires otherwise, all fire-rated doors shall be designed in accordance with NFPA, and all reinforced concrete structural members (slabs, beams, frames, columns, etc.) shall be designed in accordance with EN or international norms.

- Both substations and all associated buildings shall be equipped with fire alarm and firefighting systems meeting local regulations (see Section 11).

- Foundations and floor slabs shall have projecting galvanized earthing flags to enable connection to the earthing grid of each station.

- All substation metalwork, including transformer tanks, cable screens, feeder pillars, doors, and any internal structural steel work, shall be securely bonded together so that a firm metallic connection exists between each of them and the substation earthing terminal.

- The application of windows and glass panels, as well as the general architectural concept of the buildings and containers, is subject to the approval of the Engineer. Observations and requirements of the Employer's Representative are not grounds for additional claims by the Contractor.

Fundamental Design Criteria

The following fundamental design criteria shall be strictly followed and applied in view of the proposed equipment:

- Results of site-specific soil investigations at Qush Tepa and Darzaab

- Codes and standards adopted in the design

- Loading adopted for the various elements of the structure, load factors, and load combinations

- Description of the design method and theories adopted

The base calculation of the structural design and general arrangement drawings shall include the principal framing and loading calculations, architectural scheme design, and the expected forces in the relevant elements of the structure, to guarantee the security of the equipment in operation.

Architectural detail drawings covering the electrical equipment requirements shall include:

- Plans, elevations, and sections detailed enough to enable construction without difficulties

- Staircase details

- Roofing and waterproofing detail

- Doors and windows schedules

- Finishing schedules

Particular Space Requirements

Dimensions of switchgear rooms, control rooms, and any other rooms at both the Qush Tepa and Darzaab control buildings shall be determined under full consideration of the equipment requirements and listed in the relevant part of the Specification. Pipes, lighting installations, and air-conditioning ducts shall be located so that sufficient (shadow-free) lighting is provided after completion of all installations.

### 4.9 Cable Trenches (General)

All electrical trenches shall be of reinforced concrete. For outdoor trenches exposed to heavy loads (trucks), reinforced concrete covers, calculated for 1,000 kg/m², shall be provided. At road crossings within the Qush Tepa and Darzaab substation yards, truck loads imposed by SLW 60 (or the locally applicable equivalent) shall be considered.

Trenches shall be provided with sumps to collect stormwater inside the trenches, discharging to the site stormwater drainage system.

Reinforced concrete cable trenches, pulling pits, and duct banks shall be cast in C30 concrete and shall suit the requirements of the cable arrangements, all to the approval of the Engineer. Reinforced concrete duct banks shall be provided at all road crossings with transition chambers at each end. Ducts shall be sloped to a low point and drained. Duct banks shall consist of conduit or equivalent approved pipes with sufficient concrete cover, designed to safely carry all loads transported over the roads. Necessary fittings and inserts shall be cast in place, and slots shall be provided in the center walls of cable trenches to suit the cable arrangement requirements. Reinforced concrete pulling pits shall be constructed where required, covered with suitable covers designed to accommodate the likely loading and to permit safe removal. Pre-cast concrete covers shall be designed to support a concentrated live load of 10 kN placed anywhere on the span, with maximum deflection of 1/500 of the span.

Given the potentially saline/sulphate-bearing soils common in parts of Jawzjan Province, the Contractor shall provide additional protection for concrete from sulphate attack by applying a protective bitumen coating not less than two millimeters thick to contact surfaces, confirmed by the site-specific chemical soil analysis (see Section 13). The bitumen coating on vertical faces shall be applied in more than one layer to ensure complete absence of pinholes and bare patches.

## 5. Requirements for the Execution of Civil Works

### 5.1 General Stipulations

The specifications and methods of construction for civil works at the Qush Tepa and Darzaab Substations are given hereinafter. The Contractor shall follow and conform to these specifications and shall submit its own specifications proposed for methods not covered herein.

The quoted costs given in the lump sum price shall cover any subsidiary or incidental works found necessary.

No work will be regarded as complete until the Contractor has removed from each site all rubbish and unused materials and has properly dressed and finished the grounds to final approved levels, to the full satisfaction of the Employer.

### 5.2 Site Facilities for the Employer's Representative

For the use of Employer/Engineer's site personnel at each of the Qush Tepa and Darzaab sites, the Contractor shall provide a complete and fully equipped temporary accommodation container for two engineers and a meeting room container (containerized or hard block construction), at locations to be indicated by the Employer/Engineer, comprising:

- Employer/Engineer's accommodation containers, including furniture

- Employer/Engineer's meeting room container, including furniture

- Air-conditioning, telephone, and internet connection for the Employer/Engineer's offices

These containers shall be maintained by the Contractor throughout the project period and removed upon request after completion of works.

Minimum Room Requirements

Accommodation container: one (1) room per engineer (min. 3 × 4 m²), one (1) toilet room, and one (1) shower room.

Meeting room container: one (1) room for at least 10–12 persons (min. 8 × 4 m²).

Accommodation rooms shall be fully furnished to the satisfaction of the Employer/Engineer with air conditioning (heating and cooling), wardrobe cabinets, tables, chairs, sanitary facilities, and a kitchen equipped with a sufficiently sized refrigerator, microwave oven, and a 2-plate cooker. The meeting room shall be furnished with a large table, chairs, a desk, filing cabinets, air conditioning, a telephone system, and shall be connected to the local (Afghan) telephone system for international and local calls.

The facilities shall be provided with all necessary services (electrical energy, potable water supply, sewers, drainage system with soak pit, fire extinguishing system, etc.). The Contractor shall install an independent communication system for the Employer's/Employer's Representative's offices at each site, and shall submit all drawings and details for temporary buildings, services, and equipment for approval prior to commencing execution works.

### 5.3 Communication System

The Contractor shall install an independent communication system to the Employer's and Employer's Representatives' offices and facilities at both the Qush Tepa and Darzaab sites, comprising at least two international telephone connections and internet access.

### 5.4 Responsibilities of the Contractor

The Contractor shall be solely responsible in all respects for the suitability and stability of the buildings and foundations at both sites.

The Contractor shall also be solely responsible for verifying the suitability of its designed foundations against the effective ground conditions encountered. Where the soil excavated according to the approved design requires design modifications, these shall be carried out by the Contractor without extra charge and shall be approved by the Employer.

Construction work shall be performed to achieve high standards of quality and function. All materials shall be new and of the best quality, suitable for the climatic conditions of Jawzjan Province without distortion or deterioration.

Setting Out of the Work

The Contractor shall set out the work and shall be solely responsible for the accuracy of the setting-out, including maintenance of existing survey marks and provision of all necessary new survey marks.

Materials

All materials used in the works shall be new and of the best quality of their respective kinds, complying with the requirements of the latest edition of the relevant standards.

Workmanship

All workmanship shall be of the highest standard, performed by competent personnel skilled in their respective trades.

Samples

Samples, when approved, shall be regarded as the acceptable standard; material or workmanship not subsequently complying with the samples shall be rejected and replaced by the Contractor. Sample storage boxes shall be provided by the Contractor free of cost.

Tests

- Whenever considered necessary by the Contractor/Employer/Employer's Representative, inspectors may be sent to manufacturers' or subcontractors' facilities to test materials or supervise their manufacture.

- Where specified or requested, the Contractor shall obtain from the manufacturer certificates of test showing that the materials have been tested in accordance with this Specification and applicable standards.

Prevention of Damage

The Contractor shall take all necessary and reasonable precautions during execution of the works to prevent damage to existing land, fences, channels, roads, buildings, and services on and/or adjacent to each site.

Safety Precautions

Wherever works are to be constructed in the vicinity of existing electrical installations, overhead power lines, power cables, or any other electrical equipment in operation, the Contractor shall be responsible for ascertaining the necessary precautions and safety measures required by the rules and local Authorities.

Cleanliness of the Site

The Contractor shall at all times maintain each site in a clean condition; all rubbish and debris shall be collected and disposed of as requested.

Contractor's Area

Areas to be used by the Contractor for offices, stores, accommodation, and workshops shall be agreed with the Employer/Employer's Representative at each site. Suitable and adequate temporary sanitary facilities shall be provided for site staff, at positions agreed with the Employer/Employer's Representative. The Contractor shall take all necessary health measures for its employees and staff, as required by the works and by the statutory provisions of local Health authorities.

Water, Electricity, and Other Power

The Contractor shall be responsible for supplying all temporary water, electricity, and other power required for execution of the works from a source indicated by the Employer, and shall give notice and pay all fees required by the authorities for such supplies and services. The Employer will give necessary assistance for electricity connections.

Program

The Contractor shall prepare general overall and detailed programs for the civil works of both substations and submit them for approval, in accordance with the general and special conditions of the Contract. The Contractor shall provide adequate and qualified supervision for all civil works and subcontractors. No payment will be made to the Contractor for delays due to inclement weather conditions.

### 5.5 Site Services during Construction

Site services such as the Contractor's temporary site buildings, site fire protection, site access control and security, temporary latrines and ablutions, and temporary electricity and water supplies are the responsibility of the Contractor but shall be coordinated with the Employer or Employer's Representative.

Site Preparatory Works

The Contractor shall clear all materials and debris from the areas required for temporary and permanent works and access. Trees and vegetation, including rubbish and objectionable materials, shall be felled, stumped, stacked, burned, or disposed of, unless otherwise stated. Holes and cavities resulting from clearing, grubbing, and removal of stumps and roots shall be backfilled with acceptable materials compacted to the density of adjacent areas. Materials removed during clearing shall be burned, buried in disposal areas, or otherwise disposed of as approved by the Employer.

Any excavation of cable trenches or foundations near existing services shall be made by hand and not by excavator.

Site Clearance and Demolition Works

Site clearance and demolition works consist of the removal and disposal of bushes, existing structures and foundations, and any other obstructions on the substation sites and access roads, as well as backfilling of existing pits, trenches, and channels. Before submitting its Bid, the Contractor shall visit each site and examine the extent and nature of the works included in this section of civil works; all such works shall be included in the lump sum price offered.

Clearing and Grubbing

Clearing and grubbing shall consist of clearing all trees, bushes, and other vegetation and rubbish over the site area, as shown on the drawings or directed by the Employer, with all necessary precautions taken to prevent damage to items designated to remain undisturbed.

Demolition of Existing Structures

Demolition, removal, and storage of any existing structures to be removed shall be performed by the Contractor, who shall plan, follow up, execute, and supervise these demolition works.

### 5.6 Earthworks and Excavation

This section covers all necessary work for excavation, importing, placing, disposal, and compaction of earth as required by the drawings and specifications for both the Qush Tepa and Darzaab sites. The Contractor shall excavate to the lines, grades, and depths shown, ensuring safe side slopes and proper drainage at all times. Suitable excavated material shall be reused for backfilling or embankment construction, while surplus or unsuitable material shall be disposed of at approved locations. All fill and backfill shall be placed in layers not exceeding 250 mm loose thickness and compacted to at least 95% of maximum dry density per ASTM D698 or equivalent. The Contractor shall take all necessary precautions to prevent damage to existing structures, underground utilities, and adjacent properties. Earthwork operations shall comply with relevant national and international standards to ensure stability, safety, and long-term performance.

#### 5.6.1 General

The Contractor shall, before submitting its Bid, visit each site and inform itself about ground conditions, the nature of the soil to be excavated, and obstructions which may be encountered within the limits of excavation. No claims will be accepted after award of the Contract. Each site shall be excavated, filled, and graded to a general level established by the Contractor, taking into account the results of topographical surveys performed by the Contractor and the imposed levels relative to existing/planned structures. The quantity of imported fill from borrow pits shall be kept to a minimum.

#### 5.6.2 Water Removal

Lump sum prices shall include the costs of control and removal of water during and/or after excavation. The Contractor shall provide all facilities and take whatever action is necessary to keep excavations clear of water at all times during execution.

#### 5.6.3 Topsoil Removal

The first earthworks operation shall be removal of topsoil to a depth agreed with the Employer. Topsoil shall be kept separate from other material and stockpiled for reuse in landscaped areas, as indicated by the Employer.

#### 5.6.4 Execution of Excavations

Works shall be excavated either by hand or by mechanical excavating equipment. Excavation by hand may be required close to existing installations and/or underground services, subject to special instruction of the Employer/Employer's Representative. The Contractor shall carry out earth- and rockwork for: clearing and grubbing; excavation of topsoil; open-cut excavation; backfilling; safety precautions during earthwork; underground excavation (if required); grading; replacement of material; trench excavation for service lines; and embankments.

Safety Precaution

The Contractor shall be responsible for all necessary safety measures, including proper strutting, sheeting, and bracing, stabilization and protection of slopes, and methods of excavation to reduce risk of slides.

Over-Excavation

Where excavations are executed beyond the established lines without the Employer's/Employer's Representative's prior approval, the Contractor shall at its own expense backfill with approved material (including required compaction) or lean concrete, to the Employer's/Employer's Representative's approval. No payment shall be made for over-excavation not ordered.

Stockpiles and Disposal

Excavated material selected for reuse shall be placed immediately in its final position where possible, or otherwise stockpiled or deposited on site as directed. The Contractor shall not be entitled to additional payment for stockpiling, reuse, or carting to waste disposal areas. Material unfit for reuse, and material not required for backfilling, shall be removed from the site by the Contractor to a storage area indicated by the Employer at a distance of max. 10 km. This clause also applies to rubbish obtained from demolition works.

#### 5.6.5 Backfilling

The material used for filling shall be made with natural material free from mud, silt, vegetable, or other soft or injurious matter. The Contractor shall inform the Employer of the source or borrow pit from which it proposes to obtain material, for approval by the Employer's site engineer.

| Location | Minimum Compaction (Modified Proctor) |
| --- | --- |
| Under buildings, structure foundations, and slabs | 95% |
| Under roadways and parking areas | 98% |
| Under transformers and other major foundations | 98% |
| Embankment | 95% |

### Fill Materials

Fill materials used shall be examined by the Contractor and approved by the Employer/Employer's Representative.

Select Fill

Select fill shall be well-graded, non-cohesive, and nearly salt-free soil free of organic matter, of a nature and character that can be compacted to the specified densities, free of plastic clays and materials subject to decay, decomposition, or dissolution, or that will corrode piping or other metal. Select fill is intended for use below structures, roads, and parking areas.

Ordinary Fill

Ordinary fill shall be natural inorganic soil with salt content not greater than 5% and organic matter less than 3%, intended for use in non-built areas.

Special Fill

Special fill material shall be gravel or crushed rock, intended for use as sub-base material for open-air switchyard areas and roads. Density requirements shall be as per modified AASHTO 180 Method D or equivalent, at optimum moisture content.

Placing and Compacting

Filling shall be placed in layers not exceeding 200 mm in depth with a slight fall to allow natural drainage. Each layer shall be compacted at optimum moisture content by an 8-tonne smooth wheel roller or equivalent vibrating roller, or other approved means. Subsequent layers shall not be placed until the previous layer has been compacted as specified and accepted by the Employer. Filling material lacking sufficient moisture shall be sprayed with water until compaction can proceed at optimum moisture content.

Excavation for pits and trenches for foundations, drainage, and electrical works shall be taken out to the minimum sizes necessary and shall not be kept open longer than necessary. The Contractor shall ensure bottoms of excavation are protected from deterioration and contamination and that adjacent foundations and pipes are not undermined, damaged, or weakened. Excavation taken below proper level without approval shall be made good at the Contractor's expense using lean concrete.

The Contractor shall be responsible for the stability of steep excavation sides and shall provide and install all timbering and shoring necessary to ensure stability; shoring shall not be removed until the risk of damage from earth pressure has passed. The bottoms of excavations shall be properly trimmed, leveled, inspected, and approved by the Employer before placing concrete.

Backfilling of Structures

As soon as possible after permanent works are sufficiently hard and have been inspected and approved, backfill shall be placed and thoroughly consolidated in layers not exceeding 200 mm in depth. Materials deposited or accumulated on excavated areas due to delay, floods, bad weather, or slips shall be removed by the Contractor at its own cost, and pumping shall be provided to keep the works, including the deepest foundations, free from water. Positions of temporary sumps shall be approved by the Employer; no sumps shall be permitted within the area of the permanent works' foundations. The Contractor shall give due notice when excavation beds are properly and finally prepared, so the Employer may arrange the necessary inspection.

### 5.7 Site Finishing

Weed Killer

A weed-killer of an approved type suitable for local conditions shall be spread over areas to be covered by site surfacing before such surfacing is laid, of a type that does not cause corrosion of metals and used strictly in accordance with the manufacturer's instructions.

### Switchyard Surfacing

Site surfacing shall consist of 200 mm of clean, hard, natural gravel or crushed stone graded from 10 to 30 mm, spread after installation of service and cable earth strips and electrical equipment.

### 5.8 Shallow Foundations

#### 5.8.1 General

Foundations shall be performed according to the requirements of the specific loads and the site-specific soil investigation report. Special measures shall be taken if soil and laboratory tests indicate chemically aggressive conditions. Soil conditions met during the foundation works shall be checked by the Contractor's soil engineer, recorded, and compared with the previous investigation results; if essential differences occur, the Contractor shall inform the Employer and propose further measures. Prior to pouring concrete, the Contractor shall verify the specified soil conditions below the foundation level by a sounding.

#### 5.8.2 Drainage of Foundation Pits

During foundation works, excavated areas, foundation levels, and pits shall be kept free of water down to at least 0.5 m below the foundation level.

#### 5.8.3 Waterproofing

Necessary measures shall be taken to protect the structure against water action, e.g., in accordance with EC2, ENV 1992-1-1.

#### 5.8.4 Pit-Wall Stability

Excavated pit sides, walls, or slopes shall be stable and established with respect to safety regulations.

#### 5.8.5 Settlement and Expansion Joints

Joints shall be arranged so that stresses and strains caused by settlement, temperature, and differential settlement do not adversely affect the structures. Settlement joints shall run through the complete structure down to foundation level; expansion joints shall stop at the top level of the foundations. Joint width shall be at least 2 cm. Settlements of all relevant structures shall be measured, recorded, and shown in diagrams according to recognized standards.

##### 5.8.6 Foundations at Different Depths

Foundations at different levels shall be based beyond a load-spread angle of 30° (against the horizontal).

##### 5.8.7 Safety against Uplift

For all parts of the structures extending into groundwater, safety against uplift shall be guaranteed during all execution stages.

##### 5.8.8 Soil Replacement

If unsuitable soils are encountered below the foundation level or basement floor, they shall be replaced by suitable layer-wise compacted material down to the bearing soil.

### 5.9 Concrete Works

General

In general, concrete works shall be based on ACI, EUROCODE 1, 2, and 4, and EN/DIN standards or equivalent local and international standards and regulations.

Materials for Concrete

All materials used for concrete and reinforced concrete structures shall be of the best quality, free from defects likely to undermine strength and durability, and shall comply with agreed standards. All materials shall be stored and handled to prevent contamination and/or deterioration; deteriorated or contaminated material shall not be used and shall be removed from site at the Contractor's expense.

Cement

Cement used for concrete, reinforced concrete, mortar, grout, and plaster works shall be a moderate sulfate-resisting Portland cement in accordance with DIN 1164 or equivalent, given the sulphate-bearing soil conditions expected in parts of Jawzjan Province. All deliveries shall be accompanied by a certified mill test report including physical and chemical properties. Cement manufactured more than 6 months before the proposed delivery date shall be inspected, sampled, and tested before delivery to site. The Contractor shall obtain and provide the manufacturer's Bulk Average Test Certificate for each consignment. Samples shall be taken from each consignment and tested as directed in an approved independent laboratory. Bagged cement shall be stored in a weatherproof, clean building at all times, adequately protected against rain, humidity, and dewfall, with charging and discharging points properly sealed.

Water

Water for preparing concrete and mortar shall be clean, fresh, and free from organic and/or inorganic matter that may impair strength or durability. Water may be obtained from local sources after comprehensive testing and analysis of samples. No seawater or water from excavations shall be used. Water shall be stored in clean containers.

Aggregates

Materials used as aggregate shall be obtained from a source known to produce aggregate satisfactory for concrete, chemically inert, strong, hard, durable, of limited porosity, and free from adhering coats, clay lumps, and organic impurities. Aggregate shall comply with and be tested in accordance with applicable standards.

Concrete Additives

Concrete additives approved by the Employer/Engineer shall be used to improve consistency, workability, quality, and strength. Plasticizers and air entrainers, intended to reduce bleeding of free water at the surface, shall only be used after written approval and in accordance with manufacturer's instructions.

Concrete Mixes

Mix proportions shall be determined by proper mix design based on strength, workability, and site requirements, carried out by the Contractor's responsible specialist and approved by the Employer/Employer's Representative.

Concrete Classification

| Concrete | Cube 28 days (MPa) | Max. free w/c ratio | Max. nominal size (mm) | Min. cement (kg/m³) |
| --- | --- | --- | --- | --- |
| L | 20 | – | 25 | 280 |
| S1 | 30 | 0.40 | 20 | 380 |
| S2 | 40 | 0.40 | 20 | 400 |
| P1 | 40 | 0.40 | 20 | 400 |
| P2 | 40 | 0.40 | 20 | 400 |

Classes of Concrete

- L — Plain concrete used for lean concrete, blinding, screeds, backfill, etc.

- S1 — Reinforced concrete for general use

- S2 — Reinforced concrete in contact with groundwater

- P1 — Reinforced concrete for piles

- P2 — Precast concrete

Concrete aggregates and cement shall be proportioned and batched by weight; water and liquid additives shall be proportioned.

Trial Mixes

Before concreting commences, the Contractor shall, at its own expense, make trial mixes to determine mix proportions required to produce the specified strengths and workability, using the equipment proposed for placing, transporting, and compacting. Only materials the Contractor intends to use for concreting (including admixtures) shall be used in trial mixes. Test cubes from trial mixes shall be made and tested in accordance with approved standards. Strength requirements are satisfied if none of the cube strengths is below the required characteristic strength and the average strength of nine cubes is not less than recommended by the standards.

Consistency of Concrete

The amount of water used shall be adjusted to ensure a consistency that can be readily transported, placed, and compacted without segregation or bleeding of free water. Addition of water to compensate for stiffening before placing shall not be permitted. Consistency shall be checked by slump tests.

Mixing of Concrete

Cement and aggregate shall be thoroughly mixed in a batch-type pull mill mixer of not less than 1 m³ capacity, with total batching/mixing plant capacity sufficient to accommodate the concrete quantities to be cast continuously. Water shall not be added until all aggregate and cement are in the drum; mixing shall continue until the concrete is uniform in color and for not less than 1 minute after all materials and water are in the drum. Partly set or excessively wet concrete shall not be used. No concrete shall be mixed by hand.

Strength of Concrete

Testing of fresh concrete shall be carried out using test cubes prepared and tested for compressive strength in accordance with ACI 301 and ACI 318 or equivalent. All cubes shall be properly cast, cured, and tested to verify compliance with specified compressive strength requirements. The minimum 28-day compressive strength for any concrete class shall not be less than 30 MPa under any circumstances. Cube tests shall be performed by an accredited laboratory, with results submitted to the Engineer for review and approval. Concrete failing to achieve required strength shall be subject to further evaluation and corrective measures as directed by the Engineer.

A minimum of six test cubes shall be made on each concreting day (from the same mix) and for at least 40 m³ of concrete mixed. For columns, beams, and cantilevers, seven cubes for every 15 m³ of concrete poured shall be taken. Molds for test cubes shall be made of steel, and tests carried out in an approved laboratory.

The strength level of each type of concrete shall be evaluated separately and considered satisfactory if any individual strength test result is greater than 85% of the specified minimum cube strength (characteristic strength). If results are less than specified, the Employer/Engineer must suspend all concreting work and order further tests. Concrete not complying with the Requirements shall be broken out and replaced to the satisfaction of the Employer/Engineer. The Contractor shall pay all costs of making, curing, delivering, and testing concrete cubes.

Transport of Concrete

Immediately after mixing, concrete shall be conveyed to the place of use as rapidly as possible, using methods that prevent segregation, loss, or contamination. Concrete shall be placed and compacted within 90 minutes of the addition of water to the mix; any concrete left unplaced after this time shall be rejected and removed from the site.

Concreting Operations and Inspection before Concreting

All concreting methods shall be subject to the approval of the Employer/Engineer. Concrete placing shall not start until the Employer/Engineer has approved all preparation of forms, reinforcement, joints, and mixing, conveying, spreading, curing, finishing, and protection equipment.

Placing of Concrete

Concrete shall be placed in the forms as close as possible to its final position in a single operation to the full thickness of slabs and beams, and placed in horizontal layers not exceeding 2.5 m height in a single pour in walls, columns, and similar members. The Contractor shall organize pouring so that once concreting of a section has started, the operation is continuous, and each operation is completed prior to a stoppage.

The temperature of concrete shall not exceed 30°C measured at discharge into the works. Concrete shall not be placed when the ambient temperature is 40°C or above, or is above 37°C and rising — a provision of particular relevance given the hot summer conditions in Jawzjan Province.

Where specified, construction, expansion, or contraction joints shall be provided, and concrete poured continuously between two adjacent joints. Stoppage (cold) joints formed between two concreting operations separated by more than 6 hours shall be subject to the same treatment as construction joints.

Concrete shall not be placed by free fall from a height exceeding 2 meters; where greater heights are required, suitable trunking or chutes shall be used subject to Employer/Engineer approval. Concrete that has partially hardened shall not be exposed to injurious vibration or shock, except for controlled re-vibration where specified.

Compaction and Mechanical Vibration of Concrete

Concrete shall be compacted by mechanical vibrators, operating within 5,000 to 10,000 cycles per minute, to obtain dense material free from honeycombing, water, and air holes. The Contractor shall ensure vibrators are used so that reinforcement is not displaced, formwork is not damaged, and no segregation is caused, while achieving complete compaction.

Finish of Concrete

The concrete face shall have the finish indicated on the drawings or in the General/Particular Technical Requirements. The finished surface shall be sound, solid, and free from honeycombing, protuberances, air holes, or exposed aggregate. No plastering, cement wash, mortar, or paint shall be applied to cover defective concrete surfaces.

Construction Joints

The number of construction joints shall be kept as low as possible, consistent with reasonable precautions against shrinkage; concreting shall be carried out continuously up to construction joints. Where necessary, joint locations shall be indicated on the drawings or agreed between Employer and Contractor before work commences. Joints shall be at right angles to the general direction of the member, taking due account of shear and other stresses. Immediately prior to recommencement of concreting on a joint, the surface shall be free from laitance and roughened to expose the largest aggregate without disturbance, and shall be clean immediately before fresh concrete is placed. A record shall be kept on site of the time and date of placing concrete in each section of the work.

Expansion and Contraction Joints

Expansion joints, contraction joints, and other permanent structural joints shall be provided in positions shown on the drawings, straight and vertical except where otherwise specified, with concrete surfaces on both sides flush. Where necessary, water stops of an approved type shall be embedded in the concrete, made of high-quality material with resilience through the service life of the structure, providing both movement accommodation and sealing, with anchor parts to ensure tightness. Complete works of fixed and welded connections shall be carried out strictly in accordance with the manufacturer's instructions.

Concreting at Night

When approval is given to carry out concreting at night or in places where daylight is excluded, the Contractor shall provide adequate lighting at all points of mixing, transportation, and placing of concrete.

Concreting in High Ambient Temperature

The temperature of mixed concrete shall not exceed 30°C. Given the high summer temperatures typical of Jawzjan Province, the Contractor shall take special measures in mixing, placing, and curing of concrete, including shading of aggregates, spraying of aggregates with water, cooling of mix constituents (introduction of ice to the mixing water), and reduction of transportation time to a minimum. Suitable measures shall be provided to prevent premature setting of concrete placed in contact with hot surfaces, and all concreting areas, formwork, and reinforcement shall be shielded from direct sun and sprayed with water when necessary.

Protective Measures for Concrete

| Location | Minimum Concrete Cover |
| --- | --- |
| Concrete parts above ground (external surface) | 50 mm |
| Concrete exposed to underground and groundwater | 75 mm |
| Slabs (internal) | 30 mm |
| Beams and columns (internal) | 40 mm |

Immediately after compaction of the concrete has finished, the Contractor shall ensure adequate protection from the weather; the concrete surface shall be covered with sacking, canvas, straw mats, or similar absorbent material, or protection sprays kept constantly moist, for at least 7 days. Curing compounds or other methods of preventing evaporation may be used if approved. Where formwork cannot be removed within 24 hours after placing, it shall be kept shaded and sprayed with water. Where large sections of concrete are poured, special precautions shall be taken to reduce and dissipate the heat generated by setting and hardening (e.g., built-in cooling water pipe system).

No load of any kind shall be allowed on concrete that has not properly set, and the Contractor shall prevent any load being imposed until the concrete has been declared ready to carry loads by the Employer/Engineer.

Repair of Damaged or Defective Concrete

The Employer/Engineer shall inspect concrete after final setting; cracks, honeycomb areas, and segregation shall be marked, with no repairs carried out until directed by the Employer/Engineer.

Finishing of Concrete Surfaces

The finished surface of all concrete work shall be sound and free from defects; no plastering, cement wash, or mortar shall be applied to cover defective faces, and repair works shall be executed to the approval of the Employer/Engineer. All concrete surfaces of cable basements and similar structures endangered by groundwater shall receive a waterproofing membrane of an approved type with a protection board against the soil. All concrete in contact with soil shall receive a bituminous coating of at least two layers.

### Striking Period for Cast-in-Situ Concrete

| Element | Minimum Striking Period |
| --- | --- |
| Soffit formwork to slabs | 8 days |
| Soffit formwork to beams | 10 days |
| Vertical formwork to columns/walls | 24 hours |
| Props to slabs | 14 days |
| Props to beams | 21 days |

Extreme care shall be taken to avoid chipping of corners during removal of formwork.

Reinforcing Steel

Reinforcing steel used in reinforced concrete shall comply with EC 3 (Eurocode 3) or equivalent.

Reinforcement Supports

Reinforcement supports shall include all spacers, chairs, ties, slab bolsters, clips, chair bars, and other devices for properly assembling, placing, spacing, supporting, and fastening the reinforcement. Spacers shall be cast from concrete of the same quality as that in which they will be embedded, cast in metal molds with an approved means of separating blocks and ensuring proper size.

Certificates and Rejection

A test certificate shall accompany each consignment of steel reinforcement from the manufacturer, showing that the steel has been tested and analyzed and that such tests comply with the standards. The Employer/Engineer will reject any reinforcement steel as a result of any failed test, notwithstanding the manufacturer's certificates.

Finishing of Concrete

All exterior corners (angles of 90° or less) of reinforced concrete shall be chamfered (25 × 25 mm). The top or final surface of all concrete works shall be finished by screeding, floating, troweling, grinding, or tooling as approved by the Employer/Engineer. Dry cement or cement and sand shall not be used to dry excess water. Floors and slabs required to be finished smooth shall be troweled just before setting of the concrete.

- Screeding: executed by moving a straight edge or template by hand or mechanical means immediately after compaction

- Floating: follows screeding, not started until the concrete has begun to stiffen

- Troweling: where specified, floating shall be followed by finishing until a smooth, defect-free surface is obtained

- Grinding and tooling: shall not start until the concrete has hardened sufficiently to prevent dislodgment of aggregate

- Chiseling: wherever possible, carried out with mechanical devices

### 5.10 Formwork

Design and Construction

For stability and type of formwork and support framing used, DIN 4420 or equivalent shall be observed. The formwork and supporting structure shall be dimensioned to withstand all vertical and horizontal forces safely and shall be sufficiently rigid to maintain the forms in their correct position and true to shape and dimensions within the limits of the dimensional tolerances.

Materials for Formwork

Forms shall be constructed from steel or sound, well-seasoned timber free from shakes. Plywood lining shall be of resin-bonded, water-repellent timber. Formwork surfaces in contact with concrete shall be free from adhering grout, projecting nails, splits, or other defects. Joints shall be sufficiently tight to prevent leakage of cement grout, with connections permitting easy removal of shuttering and strong enough to retain the correct shape during consolidation. Fair-faced concrete facades shall be to the satisfaction of the Employer/Engineer, with all efforts taken to achieve a stainless finish.

Preparation and Inspection of Formwork

Before concrete is placed, all formwork shall be inspected to verify it is built according to approved plans and is clean and free from sawdust, shavings, dust, mud, earth, or other contamination, and properly oiled. Contact surfaces of panels shall be treated with a suitable release agent (e.g., non-staining mineral oil) where applicable; surfaces not oiled shall be wetted thoroughly to prevent warping.

Erection and Placing of Formwork

All formwork shall be erected and placed in accordance with the construction drawings approved by the Employer/Engineer. Shuttering shall be true to line, braced, and strutted to prevent deformation under the weight and pressure of wet concrete, live loads, wind, and other forces; deflections shall not exceed 3 mm. Formwork for walls and elsewhere shall be arranged for a maximum concreting height of 2.5 m in a single pour, with panel openings provided for cleaning, inspection, and access of vibrators as necessary. All formwork will be inspected and approved by the Employer/Engineer before concrete placing commences, without relieving the Contractor of its responsibilities under the contract.

Striking of Formwork

Formwork shall not be removed until the concrete has sufficient strength to carry its weight plus any constructional or designed loads likely to be applied, with a normal factor of safety, and shall be removed in a manner that avoids shock or injury to the concrete. Before removal, the concrete shall be examined, and removal shall proceed only under the instructions and supervision of a competent person.

### 5.11 Drainage

#### 5.11.1 Execution of Work

For trench excavation, slope safety and stability, and refilling, refer to Section 5.6 (Earthworks). For pipe laying and backfilling, the requirements of the pipe manufacturer, DIN EN 1610, or equivalent, shall be considered.

The design of the pipes shall be based on the maximum combination of loadings (external and internal) and applied systematically for the whole pipeline, subject to Employer/Engineer approval before execution. Independent of any groundwater-lowering measures, the bottom of the trench shall be kept free of water to permit satisfactory excavation, placing, and compaction. Buoyancy effects on the pipes shall be strictly avoided during construction; appropriate precautions (e.g., filters) shall prevent earth from entering the drain pipe, with mechanical filter stability ensured for all adjacent layers. All activities described below are subject to approval by the Employer/Employer's Representative.

Preparation of the Trench Bottom

The dimensions and shape of the trench bottom shall be designed to suit the required working space and type of pipe bedding. Trench bottom material must not be loosened and shall be protected against digging up, washing, and scouring. Any cohesive bottom soil that becomes loosened shall be removed to the depth of disturbance before pipes are laid and replaced by non-cohesive soil or special approved pipe bedding, compacted by layer-wise tamping or vibrating.

#### 5.11.2 Bedding of Pipes

- Type A — existing soil

- Type B — a bed of sand or gravel

- Type C — concrete support

- Type D — concrete enclosure

- Type E — special forms of construction

### Type A — Bedding on Existing Soil

Assuming the soil encountered at the pipe bottom is suitable, workable by hand, with a minimum bearing capacity of 15 N/cm², and at least medium to stiff consistency or medium density, the bedding shall be performed to correspond to the surface of the pipe, applying at least a 90° bearing angle related to the pipe centerline, without disturbing the natural density of the subsoil, and executed so the pipe is completely and uniformly supported throughout its length.

### Type B — Bedding on a Layer of Sand or Gravel

If the soil encountered is not suitable as an immediate pipe bedding, a layer of select fill shall be placed under the pipe. Sand or fine gravel used shall be well graded (max. particle size 30 mm for natural material, 15 mm for crushed stone). The bedding thickness below the lowest point of the pipe shall be at least 10 cm + 1/10 of the pipe nominal bore, compacted by suitable equipment to ensure the pipe rests firmly over the prescribed 90° bearing angle.

### Type C — Concrete Support

If the trench bottom material is unsuitable for a sand/fine gravel bedding, or where the bottom is steeply inclined, at risk of sand wash-out, or subject to local loads, the pipes shall be fully bedded on concrete. Minimum thickness of concrete bedding shall be 5 cm + 1/10 of the pipe's nominal bore, minimum 10 cm.

### Type D — Concrete Enclosure

A full concrete enclosure may be provided to increase pipe load-bearing capacity. Minimum concrete quality for pipe enclosure is B15; short reinforcing bars should bridge construction joints. It may be advantageous to subdivide the concrete enclosure by suitably spaced concrete joints at pipe connections.

#### 5.11.3 Penetrations, Supporting, and Anchoring

Penetration of pipes through buildings, shafts, thrust blocks, and other structures shall be designed so differential settlements do not occur or cannot cause leakage or damage; such penetrations shall be designed to be flexible unless otherwise approved. Pipes laid in groundwater shall be secured against uplift by anchoring or additional loads. Thrust blocks and other fixing structures shall be arranged so that the ends of pipelines remain without being subject to unrestrained forces and displacement.

Special Measures for Aggressive Water and Soils

Given the potential for aggressive soils/groundwater at parts of the Qush Tepa and Darzaab sites (to be confirmed by the site-specific chemical analysis under Section 13), pipes made from especially resistant materials shall be used, and the surfaces of pipes and joints shall be protected by special precautions where required.

Test for Water Resistance

Pipes shall be tested for water resistance before backfilling, using the manufacturer's regulations as the basis for the test.

#### 5.11.4 Embedding and Backfilling of Pipes

Until final acceptance and fill, the Contractor shall protect pipes, trench, and inspection pits from damage and obstructions. Embedding and backfilling shall not commence until pipe joints and supports are capable of being loaded by overburden and other forces, and shall be done in accordance with Section 5.6 (Earthworks), particularly regarding suitability of fill materials, compaction requirements, and quality assurance. The number of independent spot checks is limited to one per 3 km of trench length, with at least three checks performed; the Employer/Engineer may increase the number of tests if results are doubtful, at the Contractor's cost within the lump sum price.

For embedding, cohesionless select fill (max. particle size 30 mm) shall be used, deposited on both sides of the pipe up to a height of 30 cm above the pipe crown, and compacted as for select fill. Under-packing and compaction shall be carried out with the greatest possible care, using hand tamping or light mechanical compaction equipment, simultaneously from both sides to prevent pipe displacement. Any external protection (coating) on the pipeline shall not be damaged. Heavy tamping and vibrating appliances shall not be used where pipe cover is less than 1 m. Flexible pipes (e.g., glass-fiber-reinforced plastic pipes) shall be designed taking into account soil-mechanical and foundation-engineering aspects, checked against at least two different internationally recognized design methods/standards. The pipe bedding and pipe zone shall be compacted to at least 90% of modified proctor density (or 80% relative density if proctor density cannot be determined).

#### 5.11.5 Structures of the Drainage System

Shafts and Manholes

Manholes shall be provided at each inlet to the drainage system, at each change in gradient or direction, and at maximum intervals as per IPC standards. The manhole diameter shall be a function of the pipe cross-section; either prefabricated or cast-in-situ concrete manholes may be used, the latter meeting the requirements of Section 5.9 (Concrete Works). Manholes on foul water, oily water, and chemically contaminated water drains shall be rendered internally on all faces using anti-corrosive resin mastic, and all manholes shall have step irons. Manhole covers and frames shall be heavy-duty type except where flush with paved surfaces, in which case ductile iron of sufficient strength shall be used. A steel, plastic-coated ladder shall be considered for manholes with depth exceeding 1 m.

Oil Separator and Mud Trap

Oil-polluted sewage shall be led through mud traps and oil separators installed immediately outside the building before entering the sanitary sewage system. Oil separators shall comply with approved standards and be equipped with an automatic closing acoustical and optical alarm and local indication of oil to be separated; materials shall be cast iron and precast concrete pipes.

Pump Stations and Open Channels

Pump stations may be required for collection of clean drainage, stormwater from building roofs and paved areas, and cleaned sanitary sewage. They shall be constructed of cast-in-situ concrete, mainly buried in the soil; top slabs shall not be subject to traffic loads and shall be surrounded by steel railing. Open channels may be required for collection of drain/stormwater, similarly constructed of cast-in-situ concrete.

#### 5.11.6 Accessories

Manhole covers shall be made from watertight cast iron construction, with or without dirt traps, to suit local requirements. Shaft and pit covers shall have a test load suited to the traffic conditions. Trash grating dimensions shall be determined by proper structural design; trash gratings shall be of cast steel.

### 5.12 Cable Trenching

Trenching is required for the installation of all buried cables at both the Qush Tepa and Darzaab Substations.

#### 5.12.1 Outdoor Trenches

Trenches shall provide safe, durable, and accessible routing for power, control, and communication cables, constructed to prevent water ingress and allow easy drainage. Covers shall be strong enough to withstand vehicular loads where required, with adequate space provided for cable separation and future cabling.

- Slope: the bottom of the trench shall have a slope of 1% toward the nearest manhole/drain for water drainage.

- Trench walls and bed: RCC base slab constructed with M30 concrete, minimum thickness 150 mm (or more as per structural design).

- RCC walls constructed with M30 concrete, minimum thickness 200 mm (or more as per structural design).

- Trench cover: RCC precast covers with anti-slip surface finish, with a metal handle for lifting.

- Cable support system: hot-dip galvanized cable tray, cable racks/supports, brackets, and cleats.

- Joint sealing compound (bitumen-based or PU) shall be applied to precast cover joints to prevent water ingress.

- All metallic parts, including covers (if metallic), support brackets, and cable trays, shall be earthed.

- All construction shall comply with occupational safety and health regulations.

The dimensions of the trenches will be determined at the design stage according to the number of cables and applicable standards.

#### 5.12.2 Indoor Trenches

Trenches inside buildings shall be of the open type, covered by checkered steel plates (min. 8 mm thick). Indoor cable trenches in the control rooms of both substations shall be constructed from reinforced concrete with a minimum wall thickness of 200 mm and a base thickness of 200 mm, in accordance with ACI 318 standards. Trench dimensions shall accommodate all control, protection, and communication cables with at least 35% additional spare capacity. Internal surfaces shall be smooth and free of sharp edges, with radiused corners and proper alignment to avoid sharp bends. Covers shall be heavy-duty, non-slip, and flush with the floor, capable of bearing a minimum live load of 5 kN/m². Adequate drainage and moisture protection shall be ensured through sloped trench bottoms and sealed joints. Fire-resistant coatings or linings shall be applied to improve safety in case of fire. Cable segregation shall be implemented using appropriate dividers to separate different voltage and signal types. All metallic parts shall be properly earthed, and access points shall be provided for inspection and maintenance as per the relevant standards and approved drawings.

#### 5.12.3 Materials

All cable trenches shall be constructed of cast-in-situ reinforced concrete in accordance with the specifications of Section 5.9 (Concrete Works).

### 5.13 Structural Steel

Structural steel shall conform to international standards. The steel structures for switchyard equipment at Qush Tepa and Darzaab shall be designed and fabricated in accordance with IEC 61936-1, IEC 62271 series, ASTM A36 (structural steel), ASTM A123 (hot-dip galvanizing), ASTM A325 or A490 (high-strength bolts), and ASTM A153 (hardware galvanizing). Structures shall support equipment such as circuit breakers, isolators, instrument transformers, and busbars while meeting all mechanical, environmental, and electrical clearance requirements. All members shall be designed to withstand dead loads, wind loads (per ASCE 7), seismic forces (per ASCE 7 and IEEE 693), and conductor tensions, with suitable safety factors.

Galvanizing shall be applied after fabrication with a minimum coating thickness per ASTM A123 to ensure long-term corrosion resistance, given the harsh climatic exposure at both sites. Bolted connections shall follow ASTM F3125, and welding shall comply with AWS D1.1 structural welding standards. Structural analysis and design shall ensure compliance with applicable NESC or IEEE guidelines. All steel parts shall be adequately earthed per IEEE 80, and components shall be clearly labeled and marked for easy identification. Structures shall be subject to inspection, dimensional checks, and surface finish verification before erection, and installation shall follow approved shop and layout drawings — 900 g/m² galvanizing on steel sections 5 mm thick and over, 600 g/m² on steel sections 2–5 mm thick.

Bolts, nuts, and welding joints shall conform to approved standards.

## Structure Types

The steel structures in the 220 kV and 20 kV switchyards at Qush Tepa and Darzaab typically include, but are not limited to, the following:

- Circuit breaker support structures

- Current transformer (CT), potential transformer (PT), and CVT structures

- Lightning arrester (LA) structures

- Isolator structures (with and without earth switch)

- Gantry towers and portal structures

- Equipment mounting structures

- Cable support frames and marshalling box stands

- Auxiliary support structures (e.g., lighting poles, earthing supports)

Design Considerations

- All structures shall be self-supporting and capable of withstanding dead loads, equipment loads, wind loads, seismic loads, and erection/maintenance loads.

- Wind and seismic loading shall be considered based on site-specific climatic and geotechnical data for Qush Tepa and Darzaab respectively.

- Minimum clearance from live parts to ground and between phases shall comply with IEC or IEEE recommendations for 220 kV and 20 kV systems.

- The deflection of structures under maximum load shall not exceed 1/150 of the structure height.

Deflection Limits

The following maximum deflection limits shall apply under service load conditions (DL + WL or DL + SL):

| Structure Type | Maximum Permissible Deflection |
| --- | --- |
| Vertical columns/supports | H / 150 (H = height of column) |
| Cantilever arms | L / 100 (L = cantilever length) |
| Busbar gantries/portals | L / 200 (L = span between supports) |
| Equipment support (e.g., breaker, CT) | ≤ 10 mm (under working load) |
| Lightning masts (top sway) | H / 100 (under wind load only) |

Material Specifications

Structural Steel

- Hot-rolled structural steel conforming to ASTM A36 and EN 10025 Grade S275/S355 or equivalent standards

- High-tensile bolts: hexagonal head bolts of grade 8.8 or equivalent

- Washers: flat and spring lock washers as per international engineering practice

Anchor Bolts

- Steel rods with nuts and washers suitable for grouting into foundations

- Supplied with protective sleeves

Bolted Connections

- Preferably used for field assembly

- Minimum bolt diameter: 16 mm (for structural connections)

- All bolts to be tightened using torque wrenches to prevent loosening

Surface Protection — Hot-Dip Galvanizing

- All fabricated steel structures shall be hot-dip galvanized after fabrication

- Minimum zinc coating thickness: 85 microns or 610 g/m²

- The galvanizing process shall ensure full coverage of internal surfaces, holes, and corners

Factory Acceptance Test (FAT)

The FAT shall be conducted at the fabrication facility before dispatch to verify compliance with approved drawings, material standards, fabrication quality, and galvanizing protection. The test shall be witnessed by the Employer or its representative.

### 5.14 Grouting Works

Non-shrinking grout will be used for the heavy steel structure base plates. In general, all grouts used in these works shall be according to applicable standards. A grout is regarded as 'non-shrinking' if, after hardening over a period of 28 days during which the test specimens have been completely protected against drying, evaporation, and carbonation, and exposure to temperatures outside the range of 25°C ± 5°C, its volume is still not less than the initial volume.

Grout shall comprise only ready-to-use grouting material and water, mixed in accordance with the manufacturer's requirements using paddle-type mortar mixers. All defective concrete, laitance, dirt, oil, grease, and loose material shall be removed from the concrete foundation by bush hammering, chipping, or other approved means until sound, clean concrete is obtained. The surface shall be left reasonably rough but not so rough as to interfere with the proper placing of the grout.

### 5.15 Finishing Works

Floor and Wall Finish

The following table of buildings, rooms, and finishes is not necessarily comprehensive, as it depends on the final layout for the Qush Tepa and Darzaab control buildings. Any buildings or rooms not included, or special items, must be agreed with the Employer/Engineer but should fall into the same categories used elsewhere for standardization.

Floor Finishes (typical)

| Room / Area | Floor Finish |
| --- | --- |
| Switchgear rooms | Epoxy screed (trowel-applied, min. 5 mm thick) with epoxy seal coat |
| Rest room, toilets, kitchen, mess room | Glazed non-slip fully vitrified ceramic tiles |
| Offices | Heavy-duty parquet or PVC sheeting |
| Corridors, stairs, landings | 9 mm non-slip fully vitrified ceramic tiles |
| Battery rooms | Acid-resistant ceramic tiles |
| Electrical equipment areas | Heavy-duty PVC sheeting on false floor |
| A/C plant rooms, instrument/electrical workrooms | Heavy-duty PVC / rubber-backed tiles |
| Basements | Carborundum, non-slip 3 mm self-leveling epoxy screed |
| Stores, workshop, mechanical work room | Heavy-duty PVC / rubber-backed tiles |
| Transformer pits | Dust-proof, hard-wearing epoxy coating |

Internal wall finishes (typical) shall be plaster (or similar approved) and paint for control rooms, MV/LV switchgear rooms, LVAC rooms, computer rooms, restrooms, administration areas, offices and similar rooms, corridors, instrument and electrical workrooms, mechanical workrooms, and store rooms. Skirting shall be provided from the same material as the floor finish. Fair-faced brickwork shall receive cement wash and paint. Glazed ceramic tiles up to slab level shall be applied in toilets, washrooms, and kitchens.

### 5.16 Stone and Brick Masonry

Stone and brick masonry work shall be executed using high-quality natural stone and clay bricks, respectively, in accordance with the project drawings and specifications. All clay bricks shall conform to ASTM C62, while natural stone shall meet the project's quality requirements. Mortar for masonry shall be composed of Portland cement (ASTM C150), clean sand (ASTM C144), and potable water, mixed in proper proportions — typically a 1:4 ratio (cement to sand) — to ensure adequate bonding and durability. Masonry units shall be laid true to line, plumb, and level, with joint thickness not exceeding 10 mm, ensuring full bedding and uniform joints. Reinforcement and control joints shall be provided as specified in the design documents. Curing of masonry shall be maintained for a minimum period of 7 days. All work shall be subject to inspection and approval by the supervising engineer and shall comply with applicable local building codes, safety standards, and relevant ASTM and ACI requirements.

Execution

Masonry work — arranging and bedding bricks, stone, and boards — shall be executed in mortar to form a homogeneous mass, bonding materials so that point or other loads and stresses are dispersed and distributed through the mass without the structure tending to disintegrate.

Construction during Hot Weather and Cold Weather

Precautions shall be taken to prevent the work drying too quickly, particularly given the hot summers experienced in Jawzjan Province. All bricks, blocks, and boards shall be saturated before bedding, except during frost, to prevent absorption of moisture from the mortar and to remove loose dust. Brickwork or block/board work not thoroughly wetted, detectable by a thin crack between the unit and mortar joint, shall be pulled down and rebuilt. All masonry work shall be suspended during extreme weather unless adequately protected — a particular consideration given the cold winters at both sites.

Auxiliary Work

Unless specified otherwise, all work, materials, services, and safety measures, together with all tests and samples required for completion, shall be included in the offer, including: provision and walling-up of scaffolding holes and supports for beams, girders, and ceilings; walling-in or grouting of girder and beam heads and other structural members; provision of slots, grooves, and small openings; provision of scaffolding for use by others; and design calculations and drawings as far as required.

Quality Assurance

Quality assurance for brick and stone masonry shall ensure all materials comply with relevant ASTM standards and project specifications. Masonry units must be inspected for uniformity, strength, and absence of defects before use. Mortar mixing, application, and curing shall follow prescribed ratios and durations to achieve design strength. Workmanship shall maintain proper alignment, joint thickness, and bonding for structural integrity and aesthetics. Non-conforming materials or workmanship shall be rejected or rectified promptly.

Mortar

Mortar for brick work shall be cement mortar in the proportions 1:3 to 1:4 (cement and sand), mixed in a power-driven mixer, with all materials screened before mixing to remove lumps. Mortar shall be mixed only in sufficient quantity for the work immediately in hand, and no partly set mortar shall be used.

Damp Courses

Damp courses shall be laid on and bedded in a bed of 1:4 cement mortar in as long lengths as practicable. At ground floor levels, the damp-proof course for a wall shall extend to the full width. Damp-proofing under the floor slab shall be a one-layer self-adhesive bituminous membrane, 3 mm thickness, polyester reinforced, applied on bituminous primer over blinding concrete and protected from the top by a minimum 50 mm thickness cement sand screed.

Dimensions of Masonry Walls

The thickness of walls, all exclusively constructed as double-skin walls, shall be designed and constructed, including insulation boards, to meet at least a heat transmission coefficient of U = 0.65 W/(m²·K), appropriate for the extreme seasonal temperature range in Jawzjan Province.

### 5.17 Non-Structural Steelwork

#### 5.17.1 Description

Work includes all labor, materials, equipment, and services required to complete all steel work shown on the drawings and specified herein, including but not limited to: anchor bolts, leveling plates, and shim packs with complete instructions and templates to facilitate installation; base plates, columns, beams, girders, bracing, hangers, and related connections (bolted and welded); floor plating; supports for equipment or elements from other supplies; corrosion protection; temporary erection bracings and supports; and miscellaneous steel structures (ladders, rails, etc.). Unless specifically excluded, this includes furnishing and installing of all structural steel work indicated on the drawings, specified, or obviously needed to make the work of both substations complete.

#### 5.17.2 Quality Assurance

Except as otherwise specified herein, the work shall be in accordance with the approved Standards and Regulations.

#### 5.17.3 Material

All ferrous materials, their dimensions, forms, weights, tolerances, chemical and mechanical properties, shall comply with the relevant standards or approved equivalents. All work shall be carried out in accordance with the requirements of the drawings and specification; all parts in the assembly shall fit accurately together, and corresponding parts should preferably be interchangeable. Forced correction to fit members together will not be allowed. The Contractor shall submit to the Employer for approval the country of origin and manufacturer of the steel it proposes to supply.

All steelwork shall be smooth, undeformed, straight, and free from cracks, twists, and burrs. All steel shall be carefully stored and handled so that pieces are not subjected to excessive stress or damage, stored on site free from earth and dirt and properly drained. The Contractor shall be responsible for the correctness of its shop details and site connections. In the event of damage, the Contractor shall immediately undertake all repairs and replacements necessary, subject to Employer approval, at no additional cost to the Employer.

Technical Requirements

Site joints for the structure shall be bolted, unless site-welding is approved by the Employer. Construction methods shall permit easy erection and conform to the stipulations given elsewhere in these specifications. Maximum dimensions and weight of structure elements shall be limited by local transport conditions applicable to Jawzjan Province, to be investigated and verified by the Contractor.

Structural steel primer paints shall be those of a recognized manufacturer experienced in coatings, submitted to the Employer for approval before use. All other materials required for a complete and proper installation of structural steel shall be new, free from rust, first quality, and subject to review and approval by the Employer.

Prior to installation of this subsection, the installed work of all other subsections must be carefully inspected and verified as complete up to the point where this installation may properly commence. It shall be verified that structural steel may be fabricated and erected in strict agreement with the original design, approved drawings, and related standards.

### 5.18 Wall Covering

Wall coverings are to match the function of the rooms and wall areas concerned. A high standard shall be applied to the choice of materials, in particular for the control room. Reference is made again to the importance of cleanliness with a view to the removal of dirt.

### 5.19 Rendering

All rendering work shall be protected from direct sunlight during execution and curing. The Contractor shall ensure that all surrounding building work and paving is protected from cement splashes. All electrical conduits and other services shall be fixed in position, and where necessary, securely fixed in chases and recesses, before execution of any rendering or similar work.

### 5.20 Corrosion Protection of Steel and Ironwork Generally

Galvanizing

All steel and ironwork is to be galvanized. Site drilling or cutting of steel will generally not be permitted.

Shop Painting

With the exception of steelwork to be encased in concrete or galvanized, all surfaces of steelwork shall be shot-blasted to a commercial gray finish to a profile height of 40 microns minimum, then painted with one epoxy metallic zinc holding primer of an approved type and make, within one hour after shot-blasting. Surfaces of steelwork that will not be accessible after fabrication (e.g., back angles) shall be painted with two coats of red lead and two coats of micaceous iron oxide paint. All areas of painted surfaces shall be made good of any damage occurring during stockpiling and delivery to site prior to erection.

Site Painting

All materials shall be the best of their respective kinds, supplied from an approved manufacturer, and suitable for the climatic conditions of the site. Materials shall be delivered direct from the manufacturer to the site in sealed containers with maker's name and brand clearly displayed, and stored to comply with all requirements for preservation of the paints. If painting work deteriorates from any cause other than mechanical damage by others, the Contractor shall thoroughly remove the damaged paint work and repaint the area affected in accordance with the Specification, to the satisfaction of the Employer. A color schedule for all painting works will be made available to the Contractor prior to commencement of the works.

### 5.21 Raised Modular Floors

Full-access raised, easily removable, modular floor comprised of 800 × 800 mm (or 600 × 600 mm) panels shall be used. Props shall be of rust-proof material, with a screw device for level adjustment. Panels shall be of galvanized steel with a core of processed timber, with a PVC tile surface covering. The underside and edges of the panels shall be fire resistant, meeting the requirements of BS 6266 or equivalent. Panel lifting devices belong to the scope of supply of the Contractor.

### 5.22 Floor Coverings

Floor coverings are to be constructed with the desired slope or completely level. All pretreatment of the base (e.g., application of damp-proof membranes of insulating coats and adherent coatings) is to be carried out to avoid any deficiencies or damage; openings are to be edged with suitable sections.

Screeds

Screeds must be constructed to the necessary quality for the application concerned; all necessary measures are to be taken to guard against over-rapid drying-out, given the dry summer conditions typical of Jawzjan Province. Minimum thickness is 30 mm. Edgings are to be made with properly fixed steel angles.

### 5.23 Roofs

Construction

The roof construction is to be such that, with due allowance for the local climatic conditions and intended use of the rooms, no damp will penetrate the materials used. All roofs must have a minimum sound-absorbing index of 20 dB(A) and a maximum heat transmission coefficient of 0.57 W/m²·°C. Appropriate insulation materials shall be used to achieve these figures, given the significant seasonal temperature swing at both sites.

The sequence of layers forming the roof and their dimensioning are to be correlated with the type of substructure and the intended use of the building concerned. The roof surface is to be designed with a slope of 15–20°. All roof penetrations are to be made with metal surrounds and bonded flanges and shall be sealed. For covering, corrugated steel plates are preferred.

### 5.24 Doors and Windows

Doors

Aluminum frames shall be provided for exterior doors. All doors shall be installed by the manufacturer or its authorized representative, set plumb, square, level, and true to line, with frames set and securely anchored to the structure. Aluminum surfaces in contact with mortar, concrete, or other masonry materials shall be provided with one heavy brush coat of bituminous paint. Hardware for all doors shall be furnished and installed by the door manufacturer; all locks shall require different keys, with three keys furnished for each lock. Hardware for aluminum fittings shall, as a rule, be stainless steel.

Windows

Window frames shall be of aluminum, installed by the manufacturer or its authorized representative, set plumb, square, level, and true to line, with frames securely anchored to the structure and treated with bituminous paint where in contact with masonry materials. Hardware for all windows shall be furnished and installed by the window manufacturer. Window strips in switchgear rooms shall be installed at the level of +2.0 m; the same principle applies to all other areas where cabinets are installed. A fly screen shall be considered for all external windows.

### 5.25 Glazing

Clear safety toughened glass, 8 mm thick, from an approved manufacturer, shall be used for doors. For windows only, 4 mm double glazing shall be used.

### 5.26 Painting (Except Steel Surfaces)

Paints

The Contractor shall submit for approval the name of the manufacturer proposed to be used; only paints suitable for the climatic conditions of Jawzjan Province shall be used. All materials shall be delivered to the site in sealed containers displaying maker's name, specification, and date of manufacture, stored to comply with the requirements for preservation of the paints. Only colors and undercoats approved by the Employer shall be used.

Application

Application of paint shall be by brush or roller, as directed by the Employer. The treatment given to different surfaces shall be specified by the Contractor. All paint shall be applied in accordance with the manufacturer's instructions and shall not be diluted unless specifically agreed by the Employer. No external paint work shall be carried out during high winds, rains, or other unfavorable weather conditions. All rubbish and debris shall be removed and floors swept and dampened before painting commences. Door, furniture, light switch covers, and similar items shall be removed, with surrounding surfaces covered with canvas or other approved protection. Newly painted surfaces shall be protected against contamination by dust or other causes.

## 6. Geotechnical Investigations

### 6.1 General

The geotechnical study aims to understand the ground conditions necessary for a safe and cost-effective foundation design at both the Qush Tepa Substation site and the Darzaab Substation site, along with identifying any potential issues that may arise during construction. The scope of subsurface investigations conducted by the Contractor at each site must be sufficient to enable suitable foundation proposals and a satisfactory determination of the geotechnical conditions.

### 6.2 Scope of Works for Geotechnical Investigations

In order to design and construct foundations, pavements, and other substation structures at both sites, it is necessary to have precise geotechnical information and investigations. The objective of the site investigation is to precisely capture, sample, and conduct in-situ tests within each substation area, including site reconnaissance, site geology, and the site's previous utilization history, as well as aboveground and subsurface conditions.

Suggestions regarding the most suitable foundation system and alternatives, as well as the anticipated level of performance in terms of load capacity, settlement, and variations in actual conditions, shall be provided for each site.

Geotechnical recommendations for the design of the substation foundations shall address, but not be limited to, ultimate bearing resistance and depth, lateral and uplift resistance, service limit state settlement-limited bearing, and any special design requirements. Additionally, seismic design parameters shall be provided, including peak ground accelerations from earthquakes characteristic of the Jawzjan Province sites, soil profile type per standard USCS classification, earth pressure and retaining wall parameters, and the design modulus of subgrade reaction for the proposed approach.

The Contractor is required to adhere to all applicable Afghan laws, rules, and regulations relevant to the work. The most recent editions of recognized international standards and codes shall regulate the investigation procedure.

The anticipated division of work activities includes, but is not limited to:

- Site visits and on-site geophysical and geotechnical tests, including digging trial pits, drilling, testing boreholes and open pits, and installing piezometers as outlined in the exploration plan

- Classification of soils and evaluation of their geotechnical behavior, selection of appropriate samples, and conduct of geotechnical laboratory experiments

- Compilation of workstation studies, in-situ test results, lab test results, and in-situ data collection

- Generation of a comprehensive factual report including resources, procedures, acquired data, site works and lab tests, workstation study, data processing, and conclusions

- Coordination with the topographic survey to exchange information superimposable on topographic survey maps

### 6.3 Field Work

Boreholes

Exploratory boreholes shall be located at positions approved by the Employer's Representative at each of the Qush Tepa and Darzaab sites. The depth of boreholes must not be less than 10 meters, unless rock is encountered, in which case the rock thickness must be demonstrated to be greater than 1.5 meters. Boreholes must be extended to a load-bearing stratum with a minimum thickness of 3 m where unstable soils are encountered.

Boreholes will be drilled in accordance with established instructions and specifications by local, trained drillers under the direct supervision of the Contractor. To avert collapse of the borehole wall, casing shall be implemented. A suitable boring procedure ensuring continuous recovery of soil samples must be implemented, with visual examination and laboratory testing conducted on both disturbed and undisturbed samples.

Soil stratifications encountered in the boreholes shall be recorded during drilling. Borehole records must adhere to ASTM D2488 and D2487 and contain at least: the soil stratification; the number, depth, and type of soil samples; the corrected penetration resistance; groundwater levels; grain size distribution; index and engineering properties of representative samples from different strata; SPT values; and the drilling method, coring, and casing used.

Standard Penetration Tests (SPT)

Down to the depth of drilling, SPT shall be performed in the boreholes at 1.0 m intervals, in both cohesive and non-cohesive soils.

Sampling

During SPT intervals, disturbed samples shall be collected and submitted in polyethylene bags with proper identification, preserving and transporting soil samples per ASTM D4220. Undisturbed samples per ASTM D1587 shall be collected for cohesive soils at 1.5 m intervals, trimmed and sealed with non-shrinkage wax at both ends, and clearly labeled. All disturbed and undisturbed soil samples shall be sent for laboratory tests.

Groundwater Level Measurement

The water level in each borehole shall be recorded before commencement and after completion of drilling, once the water level has settled. The depth of the borehole and the casing (if any) shall also be recorded.

Cone Penetration Tests (CPT)

CPT data (per ASTM D5778) can be used to interpret subsurface stratigraphy and, through site-specific correlations, shall be carried out using static penetrometers (Dutch cone apparatus) for determination of soil type, density, and consistency.

Test (Trial) Pits (TP)

Test or trial pits down to 3.0 m shall be used as a third method of soil investigation to visually identify the top strata and its sequence, and to assess suitability for excavation. The Contractor shall obtain at least one disturbed and one undisturbed sample of each stratum encountered. The description of encountered strata and the strata sequence, accompanied by colored photographs, shall be specified in the soil investigation report.

General Soil Characteristics

A comprehensive description of the soil and subsurface shall be conducted for the investigation at each site, encompassing surface soil conditions and anticipated subsurface soil conditions (inclines, etc.), assessment of ground surface inclination, direction and stratification of cracks and fissures, and evaluation of slope stability in the event of potential sliding. This information shall be conveyed to the Employer's Representative via interim reports, allowing issuance of directives for further or supplementary investigations if required.

The minimum quantity of boreholes, soundings, or trial pits must adhere to the geotechnical design manual/standard and established references such as WSDOT, USACE Geotechnical Manual, Bowles, AASHTO, and BS, among others.

| Structure | Boreholes for Drilling | CPT (in-situ test) | Trial Pits (TP) |
| --- | --- | --- | --- |
| 220/20 kV switchyard (Qush Tepa or Darzaab) | 2–3 | 2–3 | 2–3 |
| Building zones (per site) | 2 | 2 | 2 |

The detailed method statement for geotechnical investigation must be submitted for approval, with the decision made jointly between the Contractor and the Employer or its Representative.

### 6.4 Laboratory Tests (not limited to)

| No. | Test | Standard |
| --- | --- | --- |
| 1 | Undisturbed sampling using Shelby tube | ASTM D1587 |
| 2 | Field density test (FDT) | ASTM D1556 |
| 3 | Dynamic cone penetrometer (DCP) | ASTM D6951 |
| 4 | Pile load test | ASTM D1143 |
| 5 | Plate load test for road | ASTM 1195/1196 |
| 6 | Plate load test for foundation | BS 1377 |
| 7 | In-situ California bearing ratio (CBR) | ASTM D4429 |
| 8 | Pile integrity test and analysis | ASTM D5882 |
| 9 | Percolation test | USACE Manual |
| 10 | Sieve analysis | ASTM D6913/D422 |
| 11 | Atterberg limits test | ASTM D4318 |
| 12 | Hydrometer analysis | ASTM D7928/D422 |
| 13 | Soil classification | ASTM D2487 |
| 14 | Natural moisture content | ASTM D2216 |
| 15 | Specific gravity | ASTM D854 |
| 16 | Modified Proctor test | ASTM D1557 |
| 17 | Standard Proctor test | ASTM D698 |
| 18 | California bearing ratio (CBR), lab | ASTM D1883 |
| 19 | Unconfined compressive strength | ASTM D2166 |
| 20 | Soil collapse test | ASTM D5333 |
| 21 | Consolidation test | ASTM D2435 |
| 22 | Direct shear test | ASTM D3080 |
| 23 | Chemical test of soil | ASTM D4972 |
| 24 | Chemical analysis of water | ASTM D4191, D4192 |
| 25 | Constant head permeability test | ASTM D2434 |
| 26 | Falling head permeability test | ASTM D5856 |
| 27 | Vane shear test | ASTM D2573 |

Grain Size Distribution

The specific gravity and grain size distribution of representative soil samples collected from different strata at each site shall be determined with standard sieves and a hydrometer. Grain size distribution curves with USCS classification of representative samples shall be specified in the soil investigation report.

Chemical Analyses

The groundwater and soil at both sites shall be analyzed and classified for their aggressive action on concrete. Classification shall comply with DIN 4030 or recognized standards, with results and recommendations forming part of the soil test report. Chemical analyses shall determine, as a minimum, sulfate and chloride contents and pH value.

Electrical Soil Resistivity Tests

Electrical resistivity tests shall be made for a minimum of 4 samples at each site. Soil resistivity investigation is necessary to determine soil structure; ranges of resistivity vary by soil type (clay, loam, sand, shale, etc.) and can change dramatically with moisture, temperature, and chemical content. Measurements shall be taken both horizontally and vertically. The Wenner (four-pin) method, using four electrodes driven into the earth along a straight line at equal spacing, shall be used to determine soil resistivity data for the ground grid design of each substation. Engineering judgment shall be applied to interpret the measurements and determine the uniform soil resistivity value to use in the ground grid design.

### 6.5 Results of Geotechnical Investigations

The reports for each site shall be complete and shall contain, but not be limited to, the information specified below.

Description of the Scope of Work Carried Out

- Work program

- Methods and procedures (equipment) used

- Works carried out (field investigations and laboratory tests)

Layout Location Plans of Soil Investigations

- The area

- The general layout plans

- Locations of boreholes, soundings, trial pits, and plate tests (if any) carried out

- Comprehensive map surrounds

Logs, Tables

Borehole logs shall be used to assess subsurface conditions, including the strata sequence, the nature and qualities of the strata, and groundwater conditions, together with lab test results and illustrative graphics. Borehole logs, trial pit logs, and surrounding logs shall include: actual ground level and reference to the local datum, description and limits of various soil layers, samples taken, SPT results, water levels, and depth of borehole/pit/sounding.

Soil Profiles (Cross-Sections)

The outcomes of subsoil investigations must, in addition to the drill logs, be illustrated by cross-sectional drawings, with soil profile cross-sections presented graphically and visually utilizing geotechnical software, including: actual ground level and plant datum at investigation points; SPT graphs; trial pit profiles; CPT diagrams; proposed foundation levels; limit lines of soil layers; and groundwater level legend.

Soil and Groundwater Classification

After chemical analysis, the groundwater shall be classified according to its aggressive action on concrete, in compliance with ASTM standards or equivalent codes.

Foundation Recommendation

It is necessary to provide guidance regarding the permissible bearing pressures of various types of foundations at each site. If required, the proposed type of piling foundations and their engineering values must be provided, together with an explanation of recommended strategies for improving the soil. If earthwork (cut and fill, slopes, etc.) is performed, geotechnical limits must be identified. Laboratory testing and geotechnical judgment shall be used to create recommendations for foundations, derived from the in-situ investigations.

### 6.6 Reporting

- Description of the site

- Sub-subsoil description

- Lab test results and field test results

- Boreholes log

- Water table reporting

- Geotechnical recommendation for the type of foundations and limitations for foundations

- Bearing capacity of the subsoils and subgrade modulus of the soil

- If pile foundations are recommended, calculation of piles and their load-bearing capacity for at least three different pile diameters

- Settlement analysis with complete geotechnical reports

- Geology, weather, and climate of the specific site

- Erosion recommendation and protection

- Slope stability analysis and recommendation

- Yard surfacing material recommendation and suggestions

- Seismic evaluation

- Lateral earth/soil pressures

- Earthquake impact and related parameters for the specific site

- Photographs taken during the site work

Thorough investigation reports will be generated for each site (Qush Tepa and Darzaab) in two phases. Six weeks after the soil investigation fieldwork is completed, the Contractor will provide the draft final report to the Employer's Representative for feedback and approval. The draft report will be comprehensive and will include, but not be limited to, the information outlined in Section 6.5. A final revision will be released following integration of comments and requirements.

All report deliverables, documentation, maps, and drawings must be compatible with current MS Office and CAD software formats. Data exchanged with the topographic surveyor must be provided in electronic format for subsequent electronic processing.

Safety

It is the responsibility of the Contractor to guarantee that all procedures and work are in accordance with applicable health and safety standards (e.g., OSHA or equivalent internationally recognized standard) and that the workers' health and safety are given complete consideration.

## 7. Water Supply System

The Contractor is responsible for the complete water supply system installation at both the Qush Tepa and Darzaab Substations, which includes:

- Provision and design of the whole substation water supply system as per IPC and relevant standards, including valve boxes, backflow preventers, pumps, etc.

- Designing and providing a prefabricated galvanized overhead drinking water storage tank with a capacity of 8 m³ (the SMC water tank shall be equipped with a water level indicator). The support structure shall be an RCC framed structure designed as per structural requirements and relevant standards and codes. The height of the support structure shall be calculated to provide the required pressure for the control room building. The Contractor shall obtain the Employer's approval for the SMC water tank.

- Digging a water well, minimum 12 inches diameter, to feed the overhead water tank.

- The design and construction of the water well shall be as per this specification, relevant standards, and applicable design requirements (see Section 14).

- Setting up an internal water supply system within the substation (control building and landscaping).

- Design and construction of the pump house and well house as per standard, sized so that all equipment can be placed and easily maintained; the Contractor is also responsible for the electrical and mechanical design of these structures.

- The internal water supply pipe shall be PPR PN 20, with fittings of PN 25, from an approved vendor.

- The external water pipe shall be GI heavy duty / HDPE from the water well house to the overhead water tank, and for the connection from the control building to the water tank.

- A hose bib shall be considered outside the building as per the standard and project requirements.

- The valve box for the main valve shall be considered as per design.

- The drain and overflow of the water tank shall be extended to the ground and connected to the nearest stormwater drain.

- The overhead water tank shall be insulated as per standard and Employer approval.

- Exposed pipes shall be insulated with rubber-type insulation, covered with aluminum tape; insulation thickness shall be selected as per the standard.

- For internal piping, each branch shall have a separate isolating valve.

- If a kitchen is provided in the control building, a separate water connection shall be provided for the washing machine and drinking water filter.

- The Contractor shall supply and install a drinking-water filter of an Employer-approved brand.

- All valves shall be gate-valve type, installed under the tile such that the core is easily accessible for maintenance.

- Internal piping connections shall be installed under the tile; a backflow preventer is required for the main connection, as per standard.

- For the battery room, an eye wash station and a lavatory shall be considered.

- All water supply pipes shall be leakage-tested as per IPC and relevant standards, witnessed by the Employer's representative and recorded — typically 1.5 times the design pressure, or as specified in standards such as AWWA C600 or ASTM, maintained for at least 2 hours.

- The minimum freezing protection for outside underground pipes is 80 cm from the ground surface, appropriate for the cold winters experienced in Jawzjan Province.

- The Contractor is responsible for coordination of water supply design with other sections.

- A shower tray shall be considered for showering purposes in the bathroom, and a hot water pipe shall be considered for the Muslim shower.

- A separate water heater shall be considered for the kitchen and bathroom.

- The water tank shall be equipped with a float valve, and the pump on/off shall be controlled through the automatic electrical system for filling the water tank or as per Employer approval.

## 8. Sanitary Wares

All sanitary wares (WC, lavatory, mixers, shower tray, eye wash, kitchen sink, water heater) shall be as per standard, and product catalogues must be approved by the Employer prior to procurement.

The material must be non-porous, hygienic, and corrosion-resistant (ceramic, vitreous china, stainless steel), and water consumption must comply with efficiency norms (e.g., 6/3 L dual flush for WCs). Sanitary ware materials must withstand static and dynamic loads and have smooth surfaces with minimal crevices, easy to clean.

After installation of the lavatory, WC, and shower tray, the space between the tile or ceramic surfaces shall be filled with an approved brand of silicone sealant (white color) for leakage protection.

### 8.1 Sanitary Sewage Drainage

Sanitary water from the WC, shower, wash basins, eye wash, and kitchen shall be discharged to a septic tank made of reinforced concrete. Pre-cleaned water shall be led to a soak-away pit, with a leach field considered for absorbing water from the septic tank. The leach field shall be designed as per international standards, with area sized according to space available at each site and subject to Employer approval.

The drain and vent pipe material must be PVC Sch-40, and Sch-80 for outside drainage, of an approved brand. A vent system for the piping shall be considered for internal drainage, extended up to the roof as per IPC. Black water from the WC shall be connected to the septic tank by a separate pipe. Pipe cleanouts shall be considered as per IPC. For pipe/fitting connections, weld-on solvent cement 717 of an approved brand shall be used, with pipes cleaned with a cleaner and primer of an approved brand applied prior to connection.

The drainage pipe from the kitchen shall be connected to the grease trap, then directed to the septic tank. Manholes and septic tank covers shall be heavy-duty cast iron. Vent pipes for the septic tank and grease trap shall be considered and extended to the nearest wall. The septic tank, collection box, and grease trap shall be waterproofed with an approved material.

Minimum depth for freeze protection is 80 cm; warning tape shall be considered before backfilling outside drainage pipes as per standard. All drainage pipes shall be leakage-tested as per IPC and relevant standards.

## 9. Stormwater Drainage System

The stormwater drainage system at each substation shall collect only clean stormwater, discharged into the local stormwater system or an approved on-site disposal solution. A complete, substantially maintenance-free, and operationally safe stormwater drainage system is required, including all necessary gutters, downpipes, gullies, traps, catch pits, and manholes.

Down pipes from the control building roof shall be UPVC Sch-40 of an approved brand, connected to the main stormwater system. The main drain pipe shall be HDPE or PVC Sch-80 of an approved brand; for pipe/fitting connections, weld-on solvent cement 717 of an approved brand shall be used, with cleaner and primer applied prior to connection.

A sand trap of min. 25 cm, or as specified by the standard, shall be considered in the stormwater manhole; the distance between manholes shall be as per IPC. Stormwater shall be connected to the nearest site drain; if a site drain is not available or its level is higher than the substation drain level, the Contractor shall provide a concrete ditch for evacuation of stormwater. The stormwater system shall consist of piped drains, backfilled reinforced concrete drainage ditches, and channels. Connection of the drainage systems to any existing outdoor facilities is also included in the project scope.

For the design of the stormwater drainage system, the following data shall be considered:

- The average annual precipitation shall be confirmed by local meteorological authorities for the Jawzjan Province region.

- Drain ditches shall be built in reinforced concrete, with a minimum slope of 0.2% for open drains.

- Regulations and recommendations of relevant local drainage standards shall be observed, as agreed with the Employer.

- The Contractor shall execute temporary channels as necessary to prevent flooding of the site until permanent drains have been completed.

- For design purposes, a precipitation intensity prescribed by local rules and meteorological conditions shall be considered for design of the drainage systems.

Various drains within each plant shall be arranged to avoid, as far as possible, the need for auxiliary lifting pumps. Where drainage by gravity cannot be achieved, the Contractor shall supply sump pumps, including discharge pipes for all pits, culverts, and channels, equipped with all switches and control devices as well as audible and optical alarms to prevent over-flooding in the case of failures. The boundaries of both substations shall be protected against overflooding of the site, with flood protection included in the Contractor's scope.

## 10. HVAC and Heating System Works

The control buildings at both Qush Tepa and Darzaab Substations shall be designed for cooling in summer and heating in winter, reflecting the significant seasonal temperature range typical of the region.

Split AC units shall be equipped with electrically operated air heaters to heat the supply air during winter. Condensate shall be drained into the drainage system. Room conditions shall be considered for the design of the equipment as per the standard.

The ventilation fan for the battery room shall be explosion-proof and operated by a separate electrical switch installed in an accessible area, with bird screen protection and a back-draft damper. For the exhaust fan in the toilet, a window-type EF with a back-draft damper, operated both manually and by electrical switch, shall be considered.

A hood fan shall be considered for the kitchen, with exhaust evacuated via duct or flexible pipe connected to a louver installed in the wall.

For all split units and unit heaters, a separate electrical switch shall be considered. Ventilation louvers for doors shall be considered where required, with filters installed for protection against dust and sand — a significant consideration given the dusty conditions in Jawzjan Province. HVAC systems shall also be considered for the pump house, well house, and auxiliary transformer room (if provided). The Contractor shall provide the heating and cooling load calculation in HAP software (or equivalent approved software) for each site.

## 11. Fire Detection and Protection System

This section outlines the technical specifications for the fire detection, alarm, and protection systems of the Qush Tepa and Darzaab Substation Project. The scope includes:

- Design, manufacture, and supply of fully integrated fire detection and protection systems for both substations

- Ensuring compliance with minimum stated requirements

This Section covers the technical requirements for the fire detection, alarm, and fire protection systems of both substations completely in every respect, including design, manufacturing, and supply of the complete fire protection and fire detection systems. Thereby, only the minimum requirements are stated.

The Contractor shall classify all plant areas at each site according to specific fire hazards and fire areas and shall clearly define and provide the most suitable fire protection and fire detection systems. The design, installation, and testing of the systems shall be according to local standards and NFPA standards (especially NFPA 850), whichever is more stringent.

### 11.1 Fire Risk Assessment

A fire risk assessment according to NFPA 850 shall be performed by the Contractor for each site to analyze the likelihood of fires, their consequences, and recommended mitigation measures. Special attention shall be drawn to:

- Fire prevention

- Control of ignition sources

- Definition of hazardous areas

- Construction precautions

- Fire detection and alarm systems

- Fire water supply

- Portable fire extinguishers

- Escape ways

- Other site-specific hazards

### 11.2 Fire Detection

The fire detection and fire alarm system shall comprise an automatic fire detection system installed in each room of the control building at each site, as well as where otherwise required. Signals from the detectors shall be collected in the fire alarm control panel (MCFA). Temporary fire protection and fire detection measures shall also be considered during construction. All necessary electrical instrumentation and control equipment, and all measures required by the permitting authorities, shall be included.

### 11.3 Automatic Fire Detection Systems

Each control building shall be furnished with an automatic fire detection system including an alarm control panel, connected to a fire alarm control panel in the control room. Surveillance with fire detectors shall be provided for all areas. Details of the arrangements and types of fire detectors shall be fixed in the fire protection design basis document as per the relevant standard.

### 11.4 Manual Call Points

Manual call points shall be of the break-glass type and shall be established in the control building area at emergency exits.

### 11.5 Alarm and Warning Systems

If the push button of a manual call point is pressed, an alarm shall be released and indicated immediately on the fire alarm panel in the control room. If the alarm is triggered by an installed automatic fire detector, the alarm shall be indicated first in the control room and on the fire control panel. Push-button actuation must be provided for manually operated fire alarms next to exits and on all escape routes. Sirens for indoor and outdoor installation must be provided for warning to operating personnel.

In the central control room, necessary automatic fire detectors shall be incorporated in the luminous ceiling. The whole of each substation area to be monitored shall be divided into individual alarm sections, arranged to enable rapid and positive identification of fires. Detectors installed in false floors, suspended ceilings, cable ducts, and air-conditioning or ventilation systems shall also be combined to form separate alarm sections.

Detectors belonging to a particular alarm section shall be incorporated in alarm lines, with the automatic and manual fire alarms connected via separate alarm lines to the common fire alarm control panel in the control room. The arrangement and number of detectors shall be determined by the type of fire detector used, the room configuration, and ambient conditions, as per standard. Detectors installed in inaccessible points such as cable ducts, false floors, and cable basements shall be connected in parallel to external optical alarm indicators installed close by and in readily visible positions.

No restrictions on the proper functioning of the fire alarm by reason of air movement, optical radiation, smoke, dust, vibration, or high humidity are acceptable. Fire alarms shall be located in the outgoing airflows of air-conditioning and ventilation systems. The alarm signal receiving units must be designed so that, using a standardized alarm unit socket, any type of detector may be used with equal facility on any fire alarm circuit.

The fire alarm control panel must be housed in sheet-steel enclosed cabinets, located in the control room or nearby in an appropriate location, with both optical and audible signals given when a fire alarm or fault alarm occurs. Power supply for the fire alarm system shall be taken from the station battery.

### 11.6 Fire Alarm Control Panel

The fire alarm control panel shall be implemented in electronic technology using plug-in units and assemblies on the modular construction principle, accommodated in a metal-clad enclosed panel with type IP 32 enclosure for wall-mounted/free-standing installation.

The arrangement and functioning of the fire alarm control panel shall, as a minimum, permit:

- A fire alarm and fault annunciation system designed with optical and audible alarms; the audible alarm must be resettable while the optical indication persists until the annunciation is finally extinguished or the fault cleared. If a fault warning is followed by a fire alarm annunciation, the fault indication must be stored and suppressed until the fire alarm condition has been cancelled

- Clear audible identification of the alarm/fault signal, with fire alarm and fault signals strictly segregated

- Continuous monitoring of individual fire alarm lines and function lines, and important functional groups of the panel, for faults and breakdowns, e.g., wire breakage of each alarm line, short-circuit of each alarm line, earth fault of the fire alarm system, power supply system faults, main fuse and MCB failure, and alarm modules disconnected from the plug-in frame

All fault signals shall be optically and audibly indicated. Testing facilities shall be provided for checking the functioning of the complete fire alarm system, including fire alarm lines and devices; initiation of fire alarm warnings in external facilities shall be prevented during testing, with automatic reset of the tested circuit to normal operation after testing. Simulation of all relevant fault signals, as well as all fire alarms, shall be possible.

### 11.7 Layout Display Board

A layout display board shall be provided in the control panel for indicating fire alarm and fault annunciations, including a graphic display showing a simplified ground plan of the substation, signal lamps for separate optical indication of the alarm line, and an annunciator with alarm test, reset, and acknowledge buttons.

### 11.8 Detection System Elements

Fire detector system elements and associated mountings shall be provided with sturdy, corrosion-proof plastic housings. Fire alarm detectors shall be provided with optical means for signaling activation (e.g., LED) and shall be suitable for connection of an additional optical external alarm indication. Detectors shall reset ready for operation following each alarm, without outside intervention, and shall plug in with suitable means to prevent unauthorized removal. As a minimum, ionization detectors, optical smoke detectors, flame detectors, and manual call points as described below shall be used to fulfill the requirements for each substation as a whole.

### 11.9 Ionization Detectors

For early identification of visible and invisible fire aerosols, consisting of an ionization chamber, alarm electronics, optical alarm indication, response delay pre-settable to suit ambient conditions, detector socket, and variable response sensitivity.

#### 11.9.1 Applicable Standards

- NFPA 72 — National Fire Alarm and Signaling Code

- UL 268 — Smoke Detectors for Fire Alarm Systems

- EN 54-7 — Smoke Detectors – Point Detectors Using Ionization

- IS 11360 — Indian Standard for Smoke Detectors

- CE / UL / LPCB / VdS certification required

#### 11.9.2 Detection Principle

The detector shall operate based on the ionization principle, where ionized air between two charged plates is disrupted by smoke particles, causing a change in current flow and triggering an alarm. It shall be particularly effective for detecting fast-flaming fires with minimal visible smoke.

#### 11.9.3 Design and Construction

- Type: point-type, low-profile ceiling-mounted detector

- Enclosure: high-impact, flame-retardant plastic, typically white or grey

- Base: plug-in or twist-lock mounting base (included)

- Indicator: LED to show normal (power), alarm, and fault status

- Radioactive source: Americium-241 (as per regulatory limits), securely enclosed and certified

#### 11.9.4 Electrical Specifications

- Operating voltage: 9–33 V DC

- Quiescent current: ≤ 100 µA; alarm current: ≤ 50 mA

- Output: conventional type — normally open relay contact (latching); addressable type — communicates over loop with FACP using proprietary protocol

- Reset: manual reset via FACP or power cycle

#### 11.9.5 Performance Criteria

- Response time: ≤ 10 seconds upon detecting the threshold smoke concentration

- Sensitivity: 0.5% to 2.0% obscuration/m (factory calibrated)

- Operating temperature: −10°C to +55°C; humidity: up to 95% RH (non-condensing)

- EMC: must comply with EN 50130-4 for electromagnetic compatibility

#### 11.9.6 Environmental Ratings

- Ingress protection: IP30–IP42 (indoor use)

- Installation location: suitable for clean-air indoor environments (not recommended for dusty or smoky areas)

#### 11.9.7 Maintenance and Testing

- Self-monitoring for internal circuit failure or chamber contamination

- Manual testing using test aerosol (per NFPA 72/IS 2189); LED functional test (remote or local)

- Cleaning recommended every 6–12 months, based on environmental conditions

#### 11.9.8 Compatibility

- Detectors must be fully compatible with the Fire Alarm Control Panel (FACP) model installed at the facility (conventional or addressable as required)

- Addressable detectors must support addressing via rotary switch, DIP switch, or software configuration

### 11.10 Optical Smoke Detector (Photoelectric)

For early identification of visible smoke generation, consisting of a photoelectric unit, alarm electronics, optical alarm indication, and detector socket.

#### 11.10.1 Applicable Standards

- NFPA 72, UL 268, EN 54-7, IS 11360

- CE Certification / LPCB / VdS — for internationally approved products

#### 11.10.2 Construction and Features

- Enclosure: white/grey polycarbonate or ABS, UV-resistant, IP40 minimum (higher for outdoor or dusty areas)

- Power supply: 24V DC (loop-powered for addressable systems)

- Mounting height: as per NFPA 72 and site requirements

- Base type: low-profile mounting base with tamper locking option

- Indicators: red LED for alarm, green LED for power (if applicable)

- Alarm response time: < 10 seconds after smoke detection

#### 11.10.3 Compatibility

Detectors must be compatible with the FACP brand/model used on site; protocol shall be addressable or conventional as per system design.

#### 11.10.4 Performance Requirements

- Sensitivity: 1.0% to 3.0% obscuration/m (for photoelectric)

- Operating voltage: 18–30 V DC (addressable); 9–33 V DC (conventional)

- Quiescent current: ≤ 100 µA; alarm current: ≤ 50 mA

- Operating temperature: −10°C to +55°C; humidity: up to 95% RH (non-condensing)

#### 11.10.5 Testing and Maintenance

- Automatic sensitivity testing and drift compensation (for addressable types)

- Manual test by simulated smoke test aerosol; LED functional test

- Periodic testing and cleaning per NFPA 72 / IS 2189

### 11.11 Flame Detector (UV Type)

For early identification of fire outbreaks and open flames, consisting of an optical unit, alarm electronics, optical alarm indication, detector socket, and variable response sensitivity, with the following characteristics:

- Housing: stainless steel or powder-coated aluminum, corrosion-resistant

- Enclosure rating: IP66 or IP67 for outdoor use

- Area classification: Ex d IIC T4/T6 (for hazardous areas), with ATEX or IECEx certification

- Operating temperature: −40°C to +75°C (depending on model)

- Mounting: swivel mount for directional aiming; power supply: 18–32 V DC

- Output signals: relay contacts (fire, fault, normal); 4–20 mA output (isolated); RS-485/Modbus communication (if networked)

- Alarm response time: < 3 seconds for standard fire; field of view: typically 90° horizontal, 90° vertical (model-dependent)

- Detection range: ≥ 30 meters for 1 ft² n-heptane fire (varies with type)

- Compatible controllers: must be compatible with the site FACP or fire/gas control panel

#### 11.11.1 Applicable Standards

- NFPA 72, EN 54-10, UL 268 / UL 1685

- FM/ATEX/IECEx — for hazardous area compliance

- IS/IEC 60079 — for explosive gas atmosphere classification

### 11.12 Manually Operated Push Buttons (MCP)

Consisting of a push-button, only operable after smashing the replaceable glass window fitted in the housing, painted red, with an interlocking mechanism, to be reset by key.

#### 11.12.1 Applicable Standards

- NFPA 72, EN 54-11, IS 2189, UL 38

- CE / LPCB / VdS / UL certification required for international use

#### 11.12.2 Functional Requirements

- The push button shall enable manual initiation of a fire alarm or emergency signal

- Activation shall be achieved by pressing a button or breaking a glass element (resettable or break-glass type)

- Upon activation, the unit shall send a signal to the FACP or emergency system controller

- The device shall include a visual indicator (LED) confirming activation (for addressable types)

- Enclosure: high-impact ABS or polycarbonate, color red (RAL 3000), UV resistant; ingress protection min. IP54 (IP65 outdoor)

- Mounting: surface or flush-mounted; labeling clearly marked with 'FIRE' or appropriate instruction

- Reset mechanism: key-operated or tool-based reset (for resettable type)

- Operating voltage: 18–30 V DC; operating temperature: −10°C to +55°C; humidity: up to 95% RH

- Functionality shall be verified during commissioning, including visual inspection, signal confirmation at the control panel, and reset test where applicable

### 11.13 Sirens (Audible Alarms)

This section defines the requirements for the supply, installation, and commissioning of sirens (audible alarms) for use in fire detection systems, emergency notification, or evacuation systems at both substations. The protection degree of the siren for indoor and outdoor installation must be at least IP54. Outdoor sirens are to be arranged in the transformer area; the arrangement of indoor sirens must meet site requirements for satisfactory warning of operating personnel. Control of the sirens shall be performed automatically by the fire alarm system, with manual operation from the fire control panel also possible.

#### 11.13.1 Applicable Standards

- NFPA 72, EN 54-3, UL 464, IS 2189

- CE / LPCB / VdS / UL Certification required for internationally approved models

#### 11.13.2 Functional and Electrical Requirements

- Sound pattern: continuous or pulsed tone, user-selectable where applicable, clearly audible above ambient noise in all protected areas

- Operating voltage: 24 V DC (standard); optional 230V AC for standalone or outdoor sirens

- Sound output level: indoor sirens minimum 90 dB(A) @ 1 m; outdoor sirens minimum 110 dB(A) @ 1 m

- Enclosure material: flame-retardant ABS or polycarbonate, or powder-coated metal (outdoor/industrial use); color red (RAL 3000 preferred)

- Ingress protection: indoor units IP54 minimum; outdoor/industrial IP65 or IP66

- Operating temperature: −10°C to +55°C; humidity up to 95% RH, non-condensing

#### 11.13.3 Testing and Commissioning

- Verify sound level coverage as per system design

- Functionality test with the fire alarm panel

- Tone selection and volume settings (if adjustable)

- Labeling and zone identification checks

## 12. Structural Protection

### 12.1 Material

Materials used for fire protection shall have test certificates certifying their specific application and protective function. Wherever a fire risk is possible, non-combustible building materials shall be used.

### 12.2 Fire Barriers and Fire Compartments

Fire barriers separating fire areas shall have a minimum two (2) hour fire resistance rating. All openings in fire barriers shall be provided with fire door assemblies, through-penetration seals (fire stops), or other approved means having a fire protection rating consistent with the designated fire resistance rating of the barrier. Fire door assemblies used in 2-hour-rated fire barriers shall be listed and approved for a minimum 90-minute fire rating.

All wall penetrations for piping, cables, etc. shall be refilled with non-combustible construction material. Outdoor oil-insulated transformers at both sites shall be separated from adjacent structures and from each other by firewalls, spatial separation, or other approved means to limit damage and potential spread of fire from a transformer failure.

### 12.3 Walls and Ceilings

For walls and ceilings of the buildings, only construction and insulating material of non-combustible material shall be applied.

### 12.4 Roofs

The roof cladding of the buildings shall be resistant to flying sparks and heat radiation. Roof insulation material shall be non-combustible.

### 12.5 Cable Ducts, Cable Trenches

Non-accessible cable ducts or cable trenches inside buildings shall consist of non-combustible material. Accessible cable ducts and cable trenches shall be considered as a fire-fighting compartment and shall meet fire resistance rating requirements according to the applicable standard; no self-locking doors shall be installed in cable ducts. Penetrations and fire-retarding sealing to buildings shall be designed with a fire resistance rating according to the applicable standard.

## 13. Portable Fire Extinguishers

Portable fire extinguishers shall be placed in the control buildings at both Qush Tepa and Darzaab where required, at locations specified as per design. Generally, only standardized fire extinguishers complying with local standards and NFPA shall be used.

The number, volumes, and installation locations of the fire extinguishers shall be evaluated during detail engineering, following recommendations of local standards and NFPA; CO2 fire extinguishers shall be preferred in switchgear stations and other appropriate places. The necessity for the provision of mobile fire extinguishers (50 kg) as an alternative to the fixed fire protection system of the transformers and switchyard shall also be assessed.

## Applicable Standards

- NFPA 10 — Standard for Portable Fire Extinguishers

- IS 15683 — Portable Fire Extinguishers – Performance and Construction

- IS 2190 — Code of Practice for Selection, Installation, and Maintenance

- UL/EN/BS Standards — for imported models

- CE Certification — where applicable

- Factory Mutual (FM) / Underwriters Laboratories (UL) approval preferred

### 13.1 Types of Fire Extinguishers

| Type | Agent | Use For | Size (Typical) |
| --- | --- | --- | --- |
| A | Water / Foam | Class A fires (solid combustibles) | 9 L |
| B | Foam / CO2 / Dry Chemical (ABC) | Class B (flammable liquids) | 6–9 kg/L |
| C | Dry Chemical / CO2 | Electrical fires | 4.5–6 kg |
| ABC | Mono ammonium phosphate | Multi-purpose: A, B, and C | 6 kg / 9 kg |
| CO2 | Carbon Dioxide | Electrical panels, transformers | 4.5 kg / 6.5 kg |

### 13.2 Construction and Materials

- Cylinders: seamless mild steel or stainless steel, corrosion-resistant (IS 7285 or equivalent)

- Valves: forged brass or stainless steel, chrome-plated, fitted with a pressure gauge (stored pressure types)

- Paint: red epoxy powder-coated finish with color-coded bands as per IS 15683

- Label: durable, weather-resistant, conforming to standard hazard pictograms

- Nozzle and hose: resistant to UV and chemical deterioration

### 13.3 Performance Requirements

- Operating temperature range: −5°C to +55°C (or wider for CO2), appropriate to Jawzjan Province's climate

- Discharge time: minimum 8–20 seconds (depending on type/size); discharge range: min. 2–5 meters

- Working pressure: typically 15 bar (stored pressure), 50–60 bar (CO2)

- Test pressure: 30 bar for water/foam, 250 bar for CO2

### 13.4 Mounting and Installation

- Wall-mounted or placed on proper stands at 1–1.5 m height

- Signage: fire extinguisher signs with type/class indication above each unit

- Placement: as per NFPA 10 / IS 2190 spacing guidelines (e.g., ≤ 15 m for Class A risk)

### 13.5 Inspection, Testing, and Maintenance

- All extinguishers shall be delivered with valid hydrostatic test certificates

- Initial commissioning inspection shall be carried out in the presence of the Employer or consultant

- Routine maintenance and annual servicing shall be as per IS 2190/NFPA 10

- Each extinguisher must be provided with a maintenance tag showing inspection history

### 13.6 Documentation

The supplier shall provide product datasheets and specifications, test and calibration certificates, operation and maintenance manuals, and a Material Safety Data Sheet (MSDS) for the extinguishing agent, where applicable.

## 14. Technical Specification for Water Well Construction

### 14.1 Scope

This specification covers the design, drilling, construction, development, testing, and commissioning of a borehole/water well at each of the Qush Tepa and Darzaab sites to provide a reliable water source for the control building and fire protection use. The well shall be constructed as per the relevant standard and applicable design requirements for a water well.

Existing facilities such as building structures, utilities, walks, and trees, except as otherwise specified, shall be protected from damage during construction of the wells, and if damaged, shall be repaired by the Contractor at its expense. Water pumped from the well shall be conducted to a place where it will be possible to dispose of the water without damage to property or the creation of a nuisance.

Hydrogeological and water-well information for the immediate vicinity of each site should be obtained locally from private and/or government organizations. The Driller should drill a test hole as specified to assure the water availability of the aquifer. The method of drilling and type of well construction may vary depending on the local geology of Jawzjan Province. Wells completed into unconsolidated aquifers may need to be screened depending on the type of aquifer material; if completed into consolidated (rock) aquifers, open-hole construction may be approved.

The Driller shall take all necessary precautions during construction to prevent contaminated water, fuel, or other contaminated materials from entering the well, either through the opening or by seepage through the ground surface, and shall exercise extreme care to prevent breakdown or caving of the strata overlying that from which the water is to be drawn.

The following design features are included in the water well design:

- Well casing diameter and casing materials

- Well and casing depth

- Well screen length, diameter, and slot openings

- Aquifer and well development and gravel pack material

- Collection and analysis of pump test and water quality data

- Selection of well pump

### 14.2 Selection of a Well Site

Before selecting the well location at each site, a thorough survey of the area shall be undertaken. The following information shall be obtained and considered:

- Local hydrogeology, such as terrain, soil type, depth, and thickness of water-bearing zone

- Location of nearby wells, both drilled and hand-dug, that may limit the well yield or be impacted by the new well

- Location, construction, and disposal practices of nearby sewage and industrial facilities

- Locations of sewers, septic tanks, cesspools, animal farms, pastures, and feed lots

- Chemical and bacteriological quality of groundwater, especially the quality of water from nearby wells

- Histories of water, oil, and gas well exploration and development in the area

- Location and operating practices of nearby industrial and municipal landfills and dumps

Recommended minimum distances for well sites from commonly encountered potential sources of pollution are shown in the table below. These are minimum distances serving as rough guides for locating a well from a potential source of groundwater contamination; actual distances may need to be greater depending on local geology. If at all possible, a well should be located up-gradient of any known nearby or potential sources of contamination, in consultation with local authorities. Dry wells should be abandoned and plugged in conformance with local regulations.

### Minimum Distances from Pollution Sources

| No. | Source | Minimum Horizontal Distance |
| --- | --- | --- |
| 1 | Building Sewer | 15 m |
| 2 | Disposal Field / Septic Tank | 30 m |
| 3 | Seepage Pit | 30 m |
| 4 | Dry Well | 15 m |
| 5 | Cesspool / Leaching Pits | 45 m |

### 14.3 Applicable Standards

- ASTM D5092 — Standard Practice for Design and Installation of Groundwater Monitoring Wells

- AWWA A100 — Water Wells

- ISO 14686 — Guidelines for Groundwater Development

- Local authority guidelines on well permits, groundwater protection, and abstraction limits

- Applicable national design requirements for water wells in Afghanistan

### 14.4 Site Investigation

- Conduct a hydrogeological survey to determine groundwater availability, aquifer depth and capacity, and soil/rock strata

- Prepare a well-siting report and obtain all necessary permits

### 14.5 Drilling Method

- Approved methods: rotary drilling, air rotary, or mud rotary, depending on soil type

- Drilling diameter: minimum 12" (300 mm) for production wells

- Drilling depth: based on aquifer depth, depending on site conditions

- Casing installation shall follow immediately after reaching the required depth

### 14.6 Casing and Screen

- Material: PVC Sch-80 for the casing and screen

- Casing diameter: minimum 8" (200 mm) for production use

- Well screen: slotted screen or wire-wound screen; screen slot size 0.5 mm to 1.5 mm based on aquifer analysis; placement across the water-bearing strata

- Gravel pack: washed, rounded silica sand placed between the borehole and screen to filter fine particles. The Contractor is responsible for obtaining Employer approval for all pipe, equipment, and material, and shall submit the well report as well as the sieve analysis

### 14.7 Well Development

Development shall be performed to remove fine materials and improve water inflow, using methods such as surging, air-lift pumping, and backwashing, continuing until water is clear and sand-free.

### 14.8 Pump Installation

- Type: submersible

- Capacity: sized based on required flow rate and dynamic head; the Contractor is responsible for selecting the pump size based on the well report

- Pipe connection: threaded PVC Sch-80 up to the well house; thereafter HDPE or GI Sch-40

- Pump materials: corrosion-resistant (bronze/stainless steel); include a non-return valve, control panel, and level sensors

### 14.9 Well Head Completion

- Concrete sanitary seal around casing (minimum 1 m × 1 m × 0.3 m)

- Well cap: lockable and vermin-proof

- Discharge pipe with flow meter and pressure gauge

- Surface drain to prevent standing water accumulation

### 14.10 Test for Quality of Water

During testing of the yield and drawdown test in the permanent well, the Contractor shall schedule a preliminary sample of the water in suitable containers, of sufficient quantity for bacterial, physical, and chemical analysis (TDS, pH, turbidity, hardness, bacterial content), made in accordance with the standard specified by the World Health Organization (WHO) to determine if the water is potable. 'Potable', for the purpose of this Contract, is further defined as water suitable for drinking by the public — good, clear water free from objectionable amounts of harmful bacteria and adverse chemical and physical properties, as defined by standards. Sampling shall be performed by qualified personnel who shall obtain sampling kits and schedule site visits to obtain the samples as directed. Coordination with the Employer's Representative for sampling and analysis should begin at the start of the contractual period.

### 14.11 Test for Sand

After the final well is fully developed and while the development pump is still installed, a test for sand shall be conducted. The well shall be allowed to rest for at least one hour, then pumping shall begin at the full design well yield. The Driller shall pump or bail the well until the water pumped is substantially free from clay, silt, and sand (< 8.0 mg/l) as measured by an Imhoff cone container, or until the water is clear (as determined by the Employer's Representative). Results shall be based on the average of five samples taken from a large barrel or other tank during the pump test, taken 15 minutes after the start of the test, after 25%, 50%, and 75% of the test duration, and near the end of the test. After completion of the well, unless the permanent pump is immediately installed, the Contractor shall cap the well to prevent contamination.

### 14.12 Test for Yield and Drawdown

Upon completion of the permanent production well, the Driller shall install the pump with discharge piping of sufficient size and length to conduct the pumped water to a point of safe discharge, together with all equipment necessary for measuring the rate of flow and the water level in the well. A continuous 4 to 6-hour pumping test shall be conducted with the pumping rate and drawdown recorded approximately at the intervals indicated below.

### Time Intervals for Drawdown and Recovery Readings

½ minute, 1 minute, 2 minutes, 3 minutes, 4 minutes, 5 minutes, 7 minutes, 10 minutes, 15 minutes, 20 minutes, 30 minutes, 60 minutes, 120 minutes, 240 minutes, 360 minutes.

### 14.13 Disinfection

Immediately after the well is completed, unless the permanent pump is ready for installation, the well shall be sterilized by adding chlorine or hypochlorite in such volume and strength, and so applied, that a concentration of at least 50 ppm is obtained in all parts of the well. The chlorine or hypochlorite shall be prepared and introduced into the well in a manner approved by the Employer's Representative and shall remain in the well for at least twelve hours. Section A1-10 of AWWA Specification A100 describes acceptable methods of sterilization of a well. After the contact period, the well shall be pumped until the residual chlorine content of the well water is 1 ppm or less.

# Appendix - I: Technical Data Sheets

## A. Technical Characteristics of System

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | System data |  |  |  |
|  | Plant identification system |  |  |  |
|  | Apply latest standard of | IEC | 81346 |  |
|  | KKS or AKZ shall be applied |  | yes |  |
|  | Transport assessment |  |  |  |
|  | To be performed as specified |  | yes |  |
|  | HSR Manual |  |  |  |
|  | To be submitted as specified |  | yes |  |
|  | Quality assurance plan |  |  |  |
|  | To be submitted as specified |  | yes |  |
|  | Defect reliability on painting |  |  |  |
|  | Warrantee period for painting | years | 5 |  |
|  | Fire protection measures |  |  |  |
|  | Fire protection system to be provided |  | yes |  |
|  | 220 kV system |  |  |  |
|  | Nominal system voltage Un (rms phase to phase) | kV | 220 |  |
|  | Highest system operating voltage U max. (rms phase to phase) | kV | 245 |  |
|  | Design voltage for equipment Um (rms phase to phase) | kV | 245 |  |
|  | Rated short time current (3 sec) | kA | 40 |  |
|  | Rated short circuit current making current | kA | 100 |  |
|  | System configuration (Shall be studied) |  | solidly earthed |  |
|  | Range of highest voltage for equipment (IEC 60071-1, clause 5.8) |  | II |  |
|  | Standard insulation level for equipment (B.I.L. acc. IEC 60071-1, table 2) for standard lightning impulse withstand voltage (peak) | kV | 1050 |  |
|  | Standard short duration power frequency withstand voltage | kV rms | 460 |  |
|  | Insulation coordination, latest | IEC | 60071-1, 60071-2 Clause 7.1 and 7.2 |  |
|  | Minimum creepage distance for insulation (phase to phase) | mm/kV | 31.5 |  |
|  | Range of highest voltage of equipment |  | II |  |
|  | 20 kV system |  |  |  |
|  | Nominal system voltage Un (rms phase to phase) | kV | 20 |  |
|  | Highest system operating voltage U max. (rms phase to phase) | kV | 24 |  |
|  | Design voltage for equipment Um (rms phase to phase) | kV | 24 |  |
|  | Rated short time current (3s) | kA | 25 |  |
|  | Rated short circuit current | kA | 62.5 |  |
|  | Short time power frequency withstand voltage | kV | 50 |  |
|  | Standard lightning impulse withstands voltage (peak) | kV | 125 |  |
|  | System configuration (Shall be studied) |  | solidly grounded |  |
|  | AC Frequency, rated frequency | Hz | 50 |  |
|  | 0.4 kV system |  |  |  |
|  | Nominal system voltage | V | 400/230 |  |
|  | Rated short time current (3s) | kA | 25 |  |
|  | Rated short circuit current | kA | 75 |  |
|  | System configuration (Shall be studied) |  | solidly grounded |  |
|  | 220 V DC system |  |  |  |
|  | Nominal system voltage | VDC | 220 +10/-20 % |  |
|  | 48 V DC system |  |  |  |
|  | Nominal system voltage | VDC | 48 +10/-20% |  |
|  | AC creepage distances |  |  |  |
|  | Outdoor AC equipment acc. to IEC 60815-1, Class C | mm/kV | 31.5 |  |
|  | Degree of protection of the enclosures |  |  |  |
|  | Applicable standard | IEC | 60529 |  |
|  | Indoor equipment (Except otherwise mentioned) | IP | 52 |  |
|  | Outdoor equipment (Except otherwise mentioned) | IP | 54 |  |
|  | LV network |  |  |  |
|  | TN-C-S type |  | yes |  |
|  | General requirements for earthing, lightning and potential equalizing |  |  |  |
|  | To be performed as specified |  | yes |  |
|  | Inspection and testing of substations |  |  |  |
|  | To be followed as specified |  | yes |  |

## B. Required and Guaranteed Technical Requirements and Characteristics of Equipment — 220 kV Switchyard Equipment

### 220 kV Circuit Breaker

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV Equipment |  |  |  |
|  | 220 kV Circuit Breaker |  |  |  |
|  | Applicable standard | IEC | 62271-100 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Circuit breaker type | - | Outdoor SF6 |  |
|  | Nominal voltage | kV | 220 |  |
|  | Rated voltage | kV | 245 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Rated power frequency withstand voltage | kV rms | 460 |  |
|  | Rated lightning impulse withstand voltage (1.2/50 µs) | kV peak | 1050 |  |
|  | Rated short-time current, 3s | kA | 40 |  |
|  | Rated peak withstand making current | kA | 100 |  |
|  | Rated nominal current | A | 1250, 1600 |  |
|  | Minimum creepage distance | mm/kV | 31.5 |  |
|  | First pole-to-clear factor | - | 1.3 |  |
|  | Rated operating sequence (three-phase auto reclosing) | - | 0-0.3s-CO-3min-CO |  |
|  | Maximum breaking time | ms | 60 |  |
|  | Maximum making time | ms | 100 |  |
|  | Number of tripping coils |  | 2 |  |
|  | Number of closing coils |  | 1 |  |
|  | Protection class | - | IP 54 |  |
|  | Auto-reclosing |  | single and three phase |  |
|  | Drive | - | single pole |  |
|  | Type of drive | - | spring, wound-up by electric motor or manual |  |
|  | Power supply for drive | V | 220 DC |  |
|  | Power supply for auxiliary contacts | V | 220 DC |  |
|  | Power supply for heaters | VAC | 230 |  |
|  | Test Requirements — Standard applied: IEC 62271-100, IEC 62271-1 |  |  |  |
|  | Type tests |  |  |  |
|  | Dielectric tests according to Clause 6.2 |  | yes |  |
|  | Measuring of resistance of main contacts according to Clause 6.4 |  | yes |  |
|  | Temperature rise test according to Clause 6.5 |  | yes |  |
|  | Short time withstand current and peak withstand current test according to Clause 6.6 |  | yes |  |
|  | Additional test on auxiliary and control circuits according to Clause 6.10 |  | yes |  |
|  | Mechanical operation tests on ambient temperature according to Clause 6.101.2.1 to 6.101.2.3 |  | yes |  |
|  | Short circuit making and breaking test according to Clause 6.102 to 6.106 |  | yes |  |
|  | Radio interference tests according to Clause 6.3 |  | yes |  |
|  | Verification of degree of protection test (IP) according to Clause 6.7 |  | yes |  |
|  | Single phase test according to Clause 6.108 |  | yes |  |
|  | Capacitive current switching test according to Clause 6.111.5 |  | yes |  |
|  | Routine tests |  |  |  |
|  | Dielectric tests on main circuit according to Clause 7.1 (IEC 62271-100 and IEC 62271-1) |  | yes |  |
|  | Tests on auxiliary and control circuits according to Clause 7.2 |  | yes |  |
|  | Measurement of resistance of main contacts according to Clause 7.3 |  | yes |  |
|  | Tightness test according to Clause 7.4 |  | yes |  |
|  | Design and visual check according to Clause 7.5 |  | yes |  |

### 220 kV Isolators with Earthing Switch

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV Equipment |  |  |  |
|  | 220 kV Isolators with earthing switch |  |  |  |
|  | Applicable standard | IEC | 62271-102 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Type |  | outdoor |  |
|  | Type of operation |  | center break |  |
|  | Nominal voltage | kV | 220 |  |
|  | Rated voltage | kV | 245 |  |
|  | Rated nominal current | A | 1250, 1600 |  |
|  | Rated short time current, 3s | kA | 40 |  |
|  | Rated short circuit making current | kA | 100 |  |
|  | Rated power frequency withstand voltage | kV rms | 460 |  |
|  | Rated lightning impulse withstand voltage | kV peak | 1050 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Minimum creepage distance (phase to phase) | mm/kV | 31.5 |  |
|  | Protection class | - | IP 54 |  |
|  | Drive | - | 3 pole |  |
|  | Type of drive | - | Electric motor and manual |  |
|  | Power supply for drive | V | 220 DC |  |
|  | Power supply for auxiliary contacts | V | 220 DC |  |
|  | Power supply for heater | VAC | 230 |  |
|  | Manual operating facility | yes/no | yes |  |
|  | Factory Test Requirements — Applied standard: IEC 62271-102, IEC 60694 |  |  |  |
|  | Type test |  |  |  |
|  | Dielectric tests on main, auxiliary and control circuits (IEC 60694 Clause 6.2) |  | yes |  |
|  | Radio interference voltage test (IEC 60694 Clause 6.3) |  | yes |  |
|  | Measurement of resistance of main current path (IEC 60694 Clause 6.4) |  | yes |  |
|  | Temperature rise test (IEC 60694 Clause 6.5) |  | yes |  |
|  | Short time withstand current and peak withstand current test (IEC 60694 Clause 6.6) |  | yes |  |
|  | Test to verify the degree of protection of the enclosure (IEC 60694 Clause 6.7) |  | yes |  |
|  | Test to prove satisfactory operational and mechanical endurance (IEC 62271-102 Clause 6.102) |  | yes |  |
|  | Test to prove satisfactory operation at temperature limits (IEC 62271-102 Clause 6.104) |  | yes |  |
|  | Test to prove satisfactory operation of position indication devices (IEC 62271-102 Clause 6.105 and Annex A) |  | yes |  |
|  | Test to prove satisfactory bus transfer current switching capability (IEC 62271-102 Clause 6.106 and Annex B) |  | yes |  |
|  | Routine tests |  |  |  |
|  | Dielectric tests on the main circuits (IEC 60694 Clause 7.1) |  | yes |  |
|  | Tests on the auxiliary and control circuits (IEC 60694 Clause 7.2) |  | yes |  |
|  | Measurement of resistance of main current path (IEC 60694 Clause 7.3) |  | yes |  |
|  | Design and visual checks (IEC 60694 Clause 7.5) |  | yes |  |
|  | Mechanical operations tests (IEC 62271-102 Clause 7.101) |  | yes |  |

### 220 kV Bus Bar Isolator Switch

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV Equipment |  |  |  |
|  | 220 kV Bus bar isolator switch |  |  |  |
|  | Applicable standard | IEC | 62271-102 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Type |  | Outdoor |  |
|  | Type of operation |  | center break |  |
|  | Nominal voltage | kV | 220 |  |
|  | Rated voltage | kV | 245 |  |
|  | Rated nominal current | A | 1250, 1600 |  |
|  | Rated short time current, 3s | kA | 40 |  |
|  | Rated peak withstand making current | kA | 100 |  |
|  | Rated power frequency withstand voltage | kV rms | 460 |  |
|  | Rated lightning impulse withstand voltage (1.2/50 µs) | kV peak | 1050 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Minimum creepage distance | mm/kV | 31.5 |  |
|  | Protection class of control cubicle | - | IP 54 |  |
|  | Drive | - | 3 pole |  |
|  | Type of drive | - | Electric motor and manual |  |
|  | Power supply for drive | V | 220 DC |  |
|  | Power supply for auxiliary contacts | V | 220 DC |  |
|  | Power supply for heater | VAC | 230 |  |
|  | Manual operating facility | yes/no | yes |  |
|  | Factory Test Requirements — same test regime as isolators with earthing switch above (IEC 62271-102, IEC 60694) |  |  |  |

### 220 kV Current Transformers

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV Equipment |  |  |  |
|  | 220 kV Current Transformers |  |  |  |
|  | Applicable standard | IEC | 61869-2 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Type |  | outdoor |  |
|  | Nominal voltage | kV | 220 |  |
|  | Rated voltage | kV | 245 |  |
|  | Rated current | A | 1250, 1600 |  |
|  | Rated short time current 3sec | kA | 40 |  |
|  | Rated short circuit current | kA | 100 |  |
|  | Transformation ratio for line side CT (subject to design) |  | Core 1&4: 200-400-900-1200/1A Class PX; Core 2&3: 1200-2400/1A Class PX; Core 5: 200-400-900-1200/1A Class 0.2 |  |
|  | Transformation ratio for transformer side CT (subject to design) |  | Core 1&4: 100-200-400/1A Class PX; Core 2&3: 1200-2400/1A Class PX; Core 5: 100-200-400/1A Class 0.2 |  |
|  | Rated secondary currents | A | 1 |  |
|  | Accuracy class for metering |  | 0.2 |  |
|  | Number of cores | - | 5 |  |
|  | Rated burden (subject to design) | VA | 50 |  |
|  | Minimum creepage distance | mm/kV | 31.5 |  |
|  | Rated power frequency withstand voltage | kV rms | 460 |  |
|  | Rated lightning impulse withstand voltage (1.2/50 µs) | kV peak | 1050 |  |
|  | Factory Test Requirements — Applicable standard: IEC 61869-2 |  |  |  |
|  | Type tests |  |  |  |
|  | Temperature rise test (Sub-clause 7.2.2) |  | yes |  |
|  | Impulse withstand test on primary terminals (Sub-clause 7.2.3) |  | yes |  |
|  | Wet tests for outdoor transformers (Sub-clause 7.2.4) |  | yes |  |
|  | Electromagnetic compatibility test (Sub-clause 7.2.5) |  | yes |  |
|  | Accuracy test (Sub-clause 7.2.6) |  | yes |  |
|  | Verification of the degree of protection of enclosures (Sub-clause 7.2.7) |  | yes |  |
|  | Enclosure tightness test at ambient temperature (Sub-clause 7.2.8) |  | yes |  |
|  | Pressure test for the enclosure (Sub-clause 7.2.9) |  | yes |  |
|  | Short time current test (Sub-clause 7.2.201) |  | yes |  |
|  | Routine tests |  |  |  |
|  | Power frequency voltage withstand test on primary terminals (Sub-clause 7.3.1) |  | yes |  |
|  | Partial discharge measurement (Sub-clause 7.3.2) |  | yes |  |
|  | Power frequency voltage withstand test between sections (Sub-clause 7.3.3) |  | yes |  |
|  | Power frequency voltage withstand test on secondary terminals (Sub-clause 7.3.4) |  | yes |  |
|  | Accuracy tests (Sub-clause 7.3.5) |  | yes |  |
|  | Verification of markings (Sub-clause 7.3.6) |  | yes |  |
|  | Determination of secondary winding resistance (Sub-clause 7.3.201) |  | yes |  |
|  | Determination of secondary loop time constant (Sub-clause 7.3.202) |  | yes |  |
|  | Test for rated knee point e.m.f. and exciting current (Sub-clause 7.3.203) |  | yes |  |
|  | Inter-turn overvoltage test (Sub-clause 7.3.204) |  | yes |  |
|  | Special tests |  |  |  |
|  | Chopped impulse withstand test on primary terminals (Sub-clause 7.4.1) |  | yes |  |
|  | Multiple chopped impulse withstand test (Sub-clause 7.4.2) |  | yes |  |
|  | Measurement of capacitance and dissipation factor (Sub-clause 7.4.3) |  | yes |  |
|  | Mechanical tests (Sub-clause 7.4.5) |  | yes |  |
|  | Enclosure tightness test at low/high temperature (Sub-clause 7.4.7) |  | yes |  |
|  | Corrosion tests (Sub-clause 7.4.9) |  | yes |  |

### 220 kV Capacitive Voltage Transformers

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV Equipment |  |  |  |
|  | 220 kV Capacitive Voltage Transformers |  |  |  |
|  | Applicable standard | IEC | 60044-2, 60186, 60358 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Nominal voltage | kV | 220 |  |
|  | Rated voltage | kV | 245 |  |
|  | Transformation ratio | - | 220/√3 / 0.11/√3 / 0.11/√3 |  |
|  | Rated burden secondary windings (subject to design) | VA | 100 |  |
|  | Number of cores — protection | - | 1 |  |
|  | Number of cores — measuring | - | 1 |  |
|  | Accuracy class — measuring |  | 0.2 |  |
|  | Minimum creepage distance | mm/kV | 31.5 |  |
|  | Rated power frequency withstand voltage | kV rms | 460 |  |
|  | Rated lightning impulse withstand voltage | kV peak | 1050 |  |
|  | Test Requirements — Applicable standard: IEC 60044-2 |  |  |  |
|  | Type tests |  |  |  |
|  | Temperature rise tests (Clause 8.1) |  | yes |  |
|  | Short circuit withstand capability test (Clause 8.2) |  | yes |  |
|  | Lightning impulse test (Sub-Clause 8.3.2) |  | yes |  |
|  | Wet tests for outdoor transformers (Clause 8.4) |  | yes |  |
|  | Determination of errors (Sub-Clause 12.3 and 13.6.2) |  | yes |  |
|  | Measurement of radio interference voltage (RIV) (Clause 8.5) |  | yes |  |
|  | Routine tests |  |  |  |
|  | Verification of terminal markings (Clause 9.1) |  | yes |  |
|  | Power frequency voltage withstand test on primary terminals (Sub-clause 9.2) |  | yes |  |
|  | Partial discharge measurement (Sub-Clause 9.2.4) |  | yes |  |
|  | Power frequency voltage withstand test on secondary windings (Sub-clause 9.3) |  | yes |  |
|  | Determination of errors (Clause 12.4 and 13.7) |  | yes |  |
|  | Special tests |  |  |  |
|  | Chopped impulse withstand test on primary winding (Sub-clause 10.1) |  | yes |  |
|  | Measurement of capacitance and dissipation factor (Sub-clause 10.2) |  | yes |  |
|  | Mechanical tests (Clause 10.3) |  | yes |  |

### 220 kV Surge Arresters

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV Equipment |  |  |  |
|  | 220 kV Surge Arresters |  |  |  |
|  | Applicable standard | IEC | 60099-4 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Type |  | Metal oxide |  |
|  | Nominal voltage | kV | 220 |  |
|  | Rated voltage | kV | 245 |  |
|  | Rated discharge current | kA | 10 |  |
|  | 220 kV Surge Arrester Discharge Counter |  |  |  |
|  | Type |  | outdoor |  |
|  | Counter indication |  | Digital and mechanical |  |
|  | Protection class |  | IP 54 |  |
|  | Number per three arresters |  | 1 |  |
|  | Factory Test Requirements — Applicable standard: IEC 60099-4 |  |  |  |
|  | Type tests |  |  |  |
|  | Insulation withstand test on arrester housing (Clause 7.2 and 9.7.2) |  | yes |  |
|  | Residual voltage tests (Clause 7.3) |  | yes |  |
|  | Long duration current impulse withstand test (Clause 7.4 and 9.7.4) |  | yes |  |
|  | Operating duty test (Clause 7.5 and 9.7.5) |  | yes |  |
|  | Short circuit test (Annex O) |  | yes |  |
|  | Arrester disconnectors test (Clause 7.6 and 9.7.6) |  | yes |  |
|  | Internal partial discharge test (Clause 7.8) |  | yes |  |
|  | Moisture ingress test (Clause 7.9 and 9.7.9) |  | yes |  |
|  | Current distribution test (Clause 8.1e) |  | yes |  |
|  | Bending moment test (Clause 13.7.2) |  | yes |  |
|  | Environmental tests (Clause 13.7.3) |  | yes |  |
|  | Routine tests |  |  |  |
|  | Measurement of reference voltage (Clause 2.35 and 5.2) |  | yes |  |
|  | Residual voltage test (Clause 7.3) |  | yes |  |
|  | Internal partial discharge tests (Clause 7.8) |  | yes |  |
|  | Leakage check (Clause 13.7.4) |  | yes |  |
|  | Current distribution test for multicolumn arresters (Clause 8.1e) |  | yes |  |

### 220 kV Post Insulator

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV Equipment |  |  |  |
|  | 220 kV Post Insulator |  |  |  |
|  | Applicable standard | IEC | 60168 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Type |  | porcelain |  |
|  | Operating voltage | kV | 220 |  |
|  | Highest voltage of equipment | kV | 245 |  |
|  | Rated power frequency voltage | kV rms | 460 |  |
|  | Rated lightning impulse withstand voltage | kV peak | 1050 |  |
|  | Minimum creepage distance | mm/kV | 31.5 |  |
|  | Factory Test Requirements — Type tests IEC 60168 |  |  |  |
|  | Dry lightning impulse tests (Clause 4.5) |  | yes |  |
|  | Wet power frequency withstand test (Clause 4.8) |  | yes |  |
|  | Mechanical failing load tests (Clause 5.2) |  | yes |  |
|  | Sample tests |  |  |  |
|  | Verification of dimensions (Clause 5.1) |  | yes |  |
|  | Temperature cycle test (Clause 5.4) |  | yes |  |
|  | Mechanical failing load test (Clause 5.2) |  | yes |  |
|  | Porosity test (Clause 5.6, if applicable) |  | yes |  |
|  | Galvanization test (Clause 5.7) |  | yes |  |
|  | Routine tests |  |  |  |
|  | Visual inspection (Clause 5.8) |  | yes |  |
|  | Routine mechanical tests (Clause 5.9) |  | yes |  |

### Equipment Connections — 220 kV Switchyard

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV Equipment |  |  |  |
|  | Equipment connections 220 kV Switchyard |  |  |  |
|  | Manufacturer | - | By Bidder |  |
|  | Type | - | Aluminum conductor acc. EN50182 |  |
|  | Rated current | A | As per design requirement |  |
|  | Rated short time current 3 sec. | kA | 40 |  |
|  | Factory Test Requirements |  |  |  |
|  | Type tests |  |  |  |
|  | Jointing test |  | yes |  |
|  | Stress strain curves |  | yes |  |
|  | Breaking strength of the conductors | kN/mm2 | yes |  |
|  | Routine tests — for individual wires |  |  |  |
|  | Appearance and finishing check |  | yes |  |
|  | Diameter check |  | yes |  |
|  | Conductivity check |  | yes |  |
|  | Tensile strength |  | yes |  |
|  | Wrapping |  | yes |  |
|  | Routine tests — for complete conductors |  |  |  |
|  | Appearance and finishing check |  | yes |  |
|  | Cross section area check |  | yes |  |
|  | Overall diameter check |  | yes |  |
|  | Linear density test |  | yes |  |
|  | Surface condition check |  | yes |  |
|  | Resistance test |  | yes |  |
|  | Tensile breaking strength |  | yes |  |
|  | Weight |  | yes |  |

### Overhead Conductors

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV Equipment |  |  |  |
|  | Overhead conductors |  |  |  |
|  | Type |  | ACSR |  |
|  | Manufacturer |  | By Bidder |  |
|  | Rated current | A | To be specified |  |
|  | Rated short time current 3 sec. | kA | 40 |  |
|  | Factory Test Requirements — same regime as equipment connections above (jointing, stress-strain, breaking strength, and routine wire/conductor tests) |  |  |  |

### Overhead Ground Wire

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV Equipment |  |  |  |
|  | Overhead ground wire |  |  |  |
|  | Type |  | OPGW / steel ground wire (to be confirmed at detailed design) |  |
|  | Manufacturer |  | By Bidder |  |
|  | Factory test requirements |  |  |  |
|  | Stress strain curves |  | yes |  |
|  | Breaking strength of the conductors | kN | yes |  |
|  | Routine tests — same as overhead conductors |  |  |  |

### Insulator String at 220 kV

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV Equipment |  |  |  |
|  | Insulator units |  |  |  |
|  | Applicable standard | IEC | 60383 |  |
|  | Manufacturer | - | By Bidder |  |
|  | Type | - | Cap and pin |  |
|  | Insulating body material | - | Porcelain or glass |  |
|  | Rated electromechanical or mechanical strength | kN | 160 |  |
|  | Test Requirements — Applicable standard: IEC 60383 |  |  |  |
|  | Type tests |  |  |  |
|  | Verification of dimensions (Clause 17) |  | yes |  |
|  | Dry lightning impulse test (Clauses 13,34,35) |  | yes |  |
|  | Wet power frequency test (Clause 14,34,35) |  | yes |  |
|  | Electromechanical failing load test (Clauses 18,33,1 if applicable) |  | yes |  |
|  | Thermal mechanical performance test (Clause 20,33,1) |  | yes |  |
|  | Sample tests |  |  |  |
|  | Verification of dimensions (Clause 17) |  | yes |  |
|  | Verification of displacement (Clause 21) |  | yes |  |
|  | Verification of locking system (Clause 22) |  | yes |  |
|  | Temperature cycle test (Clause 23) |  | yes |  |
|  | Electro-mechanical failing load test (Clauses 18,33,2) |  | yes |  |
|  | Mechanical failing load test (Clause 19) |  | yes |  |
|  | Thermal shock test (Clause 24, if applicable) |  | yes |  |
|  | Puncture withstand test (Clause 15) |  | yes |  |
|  | Porosity test (Clause 25, if applicable) |  | yes |  |
|  | Galvanization test (Clause 26) |  | yes |  |
|  | Routine tests |  |  |  |
|  | Routine visual test (Clause 27) |  | yes |  |
|  | Routine mechanical tests (Clause 28) |  | yes |  |
|  | Routine electrical tests (Clause 16, if applicable) |  | yes |  |
|  | Insulator tension strings |  |  |  |
|  | Rated voltage | kV | 245 |  |
|  | Rated power frequency withstand voltage | kV rms | 460 |  |
|  | Rated lightning impulse withstand voltage | kV peak | 1050 |  |
|  | Number of cap insulators per string | # | By Bidder |  |
|  | Dry lightning impulse test (Clauses 13,34,35) |  | yes |  |
|  | Wet power frequency test (Clause 14,34,35) |  | yes |  |

### 220 kV Bus Bar

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV Equipment |  |  |  |
|  | 220 kV Bus bar |  |  |  |
|  | Manufacturer |  | By Bidder |  |
|  | Type |  | Tubular |  |
|  | Rated current | A | 2400 |  |
|  | Rated short time current 3sec | kA | 40 |  |
|  | Rated short circuit current | kA | 100 |  |
|  | Nominal voltage | kV | 220 |  |
|  | Highest system voltage | kV | 245 |  |
|  | Rated power frequency withstand voltage | kV rms | 460 |  |
|  | Rated lightning impulse withstand voltage | kV peak | 1050 |  |
|  | Test requirements |  |  |  |
|  | Verification of rated current |  | yes |  |
|  | Verification of contact resistance between busbar sections |  | yes |  |

### Steel Structures, Bolts and Nuts

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV Equipment |  |  |  |
|  | Steel structures |  |  |  |
|  | Applicable standards | DIN | 17100 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Factor of safety in calculation |  | 2 |  |
|  | Galvanization thickness |  |  |  |
|  | Steel sections thicker than 5 mm | µm | 100 |  |
|  | Steel sections thicker than 2 mm to 5 mm | µm | 80 |  |
|  | Bolts and nuts | µm | 70 |  |
|  | Bolts and nuts |  |  |  |
|  | Securing with plain and spring washers |  | yes |  |
|  | Minimum quality according to DIN 267 |  | 5.6 |  |
|  | Test requirements |  |  |  |
|  | Assembly tests of gantries according to ASTM |  | yes |  |
|  | Galvanization tests |  | yes |  |

## C. Power Transformers, Auxiliary Transformers and Diesel Generator

### 220/20 kV Power Transformers

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | Power transformers, auxiliary transformers and diesel generator |  |  |  |
|  | 220/20 kV Power-Transformers |  |  |  |
|  | Applicable standard | IEC | 60076-1 |  |
|  | Instrument transformers | IEC | 60044-1 & 60044-6 |  |
|  | Power transformers | IEC | 60076 |  |
|  | Insulated bushings above 1000V | IEC | 60137 |  |
|  | Tap changers | IEC | 60214-1 & 60214-2 |  |
|  | Degree of protection for enclosure | IEC | 60529 |  |
|  | Mineral insulating oil | IEC | 60296 |  |
|  | Terminal & tapping of transformer | IEC | 60616 |  |
|  | Loading guide for transformers | IEC | 60354 |  |
|  | Tolerances for rejection | IEC | 60076-1 |  |
|  | Capability to withstand short circuits test | IEC | 60076-5 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Kind of the transformer | - | Power Transformer |  |
|  | Number of phases | # | 3 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Type of insulating |  | Mineral oil immersed |  |
|  | Location of use |  | Outdoor |  |
|  | Type of cooling |  | ONAN/ONAF |  |
|  | Temperature rise over max. ambient temperature (50°C) |  |  |  |
|  | Top oil | °C | ≤55 |  |
|  | Average winding | °C | ≤60 |  |
|  | Hot spot winding | °C | ≤70 |  |
|  | Rated power |  |  |  |
|  | HV winding | MVA | 25 |  |
|  | MV/LV winding | MVA | 25 |  |
|  | Rated voltage |  |  |  |
|  | HV winding | kV | 220 |  |
|  | LV winding | kV | 20 |  |
|  | Highest system voltage |  |  |  |
|  | HV winding | kV | 245 |  |
|  | LV winding | kV | 24 |  |
|  | On load tap changer |  |  |  |
|  | Standard applied | IEC | 60214-1 |  |
|  | Voltage ratio and tappings | kV | 220 +/- 6x1.25% / 20 |  |
|  | Contact life (operation) |  | >200,000 |  |
|  | Regulation — LV winding |  | 12 taps of 1.25% |  |
|  | Connection of windings |  |  |  |
|  | HV winding |  | Star with grounded neutral |  |
|  | LV winding |  | delta |  |
|  | Vector group |  | YNyn0d11 |  |
|  | Rated power frequency withstand voltage |  |  |  |
|  | HV winding | kV rms | 460 |  |
|  | LV winding | kV rms | 50 |  |
|  | Rated lightning impulse withstand voltage (1.2/50 µs) |  |  |  |
|  | HV winding | kV peak | 1050 |  |
|  | LV winding | kV peak | 125 |  |
|  | Neutral insulation level | kV rms | 38 |  |
|  | Rated nominal current | A | To be specified |  |
|  | Rated short-time current, 3s | kA | 40 |  |
|  | Short circuit power of the HV network |  | Infinite |  |
|  | Impedance voltage in % at 75°C winding temperature, middle tap, full load | % | 8-10, to be confirmed by system fault level analysis |  |
|  | Tolerances for penalty / rejection | IEC | 60076-1 |  |
|  | No load losses at nominal voltage and middle tap position | kW | 15 |  |
|  | Load losses at 75°C and full load, middle tap position | kW | 40 |  |
|  | No load current | % | To be specified |  |
|  | Creepage distance | mm/kV | 31.5 |  |
|  | Capability to withstand short circuits test (IEC 60076-5) |  | yes |  |
|  | Audible noise level | dB(A) | ≤65 |  |
|  | Characteristics of magnetic circuit |  |  |  |
|  | Type |  | Core type |  |
|  | Material |  | Cold rolled grain oriented silicon steel |  |
|  | Maximum flux density at rated voltage and frequency |  | ≤1.7 |  |
|  | Characteristics of bushings |  |  |  |
|  | Applicable standard |  | IEC Standards |  |
|  | Rated voltage — HV | kV | 220 |  |
|  | Rated voltage — LV | kV | 20 |  |
|  | Highest equipment voltage — HV | kV | 245 |  |
|  | Highest equipment voltage — LV | kV | 24 |  |
|  | Insulation level |  | As for the transformer |  |
|  | Number of bushings — HV + Neutral |  | 3+1 |  |
|  | Number of bushings — LV |  | 3 |  |
|  | Maximum ambient temperature | °C | 50 |  |
|  | Service altitude | m.a.s.l | Approx. 700 |  |
|  | Accessories |  |  |  |
|  | Oil conserver with filling and drainage valve |  | 1 with two sections |  |
|  | Buchholz relay |  | 2 |  |
|  | Pressure relieve device |  | 1 |  |
|  | Silica gel air dryer for the transformer |  | as required |  |
|  | OLTC to be sealed |  | Yes |  |
|  | Oil level indicator with two contacts |  | 2 |  |
|  | Oil thermometer sensor with two contacts |  | as required |  |
|  | Winding thermometer sensors with two contacts |  | as required |  |
|  | Power supply for heaters, lighting, OLTC, fans | VAC | 400/230 |  |
|  | Power supply for auxiliary contacts | VDC | 220 |  |
|  | Set of valves / Name plate / Connection diagram / Designation plates |  | yes |  |
|  | Control box for transformer and OLTC |  | yes |  |
|  | IP protection for above | IP | 54 |  |
|  | Tap position indicator |  | yes |  |
|  | Fixation on rails via metal wheels |  | yes |  |
|  | Test Requirements — Standard applied: IEC 60076-1 |  |  |  |
|  | Type tests |  |  |  |
|  | Temperature rise test (IEC 60076-2 Clause 5.2.3) |  | yes |  |
|  | Noise level (IEC 60076-10) |  | yes |  |
|  | Routine tests |  |  |  |
|  | Measurement of DC resistance (Clause 11.2) |  | yes |  |
|  | Measuring of voltage ratio and phase displacement (Clause 11.3) |  | yes |  |
|  | Measuring of short circuit impedance and load losses (Clause 11.4) |  | yes |  |
|  | Measuring of no-load losses and current (Clause 11.5) |  | yes |  |
|  | Dielectric routine tests |  |  |  |
|  | Lightning impulse withstand test (IEC 60076-3 Clause 13 & 14) |  | yes |  |
|  | Switching impulse withstand test (IEC 60076-3 Clause 15) |  | yes |  |
|  | Long duration induced AC voltage tests (IEC 60076-3 Clause 12.4) |  | yes |  |
|  | Separate source AC voltage test (IEC 60076-3 Clause 11) |  | yes |  |
|  | Separate source DC withstand voltage test incl. PD (IEC 61378-2 Clause 10) |  | as applicable |  |
|  | Auxiliary wiring test (IEC 60076-3 Clause 10) |  | yes |  |
|  | Tests on on-load tap changer (IEC 60076-1 Clause 11.7) |  | yes |  |
|  | Special tests |  |  |  |
|  | Short circuit test or calculation according to IEC 60076-5 |  | yes |  |

### Auxiliary Transformers

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | Power transformers, auxiliary transformers, and diesel generator |  |  |  |
|  | Auxiliary transformers |  |  |  |
|  | Applicable standard | IEC | 60076-1 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Kind of the transformer | - | Distribution transformer |  |
|  | Number of phases | # | 3 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Type of insulating |  | Mineral oil immersed (IEC 60296) |  |
|  | Location of use |  | indoor |  |
|  | Type of cooling |  | ONAN/ONAF |  |
|  | Rated power |  |  |  |
|  | HV winding | kVA | 250 |  |
|  | LV winding | kVA | 250 |  |
|  | Rated voltage |  |  |  |
|  | HV winding | kV | 20 |  |
|  | LV winding | kV | 0.4 |  |
|  | Highest system voltage |  |  |  |
|  | HV winding | kV | 24 |  |
|  | LV winding | kV | 0.6 |  |
|  | Connection of windings |  |  |  |
|  | HV winding |  | delta |  |
|  | LV winding |  | Star with grounded neutral |  |
|  | Rated power frequency withstand voltage |  |  |  |
|  | HV winding | kV rms | 50 |  |
|  | LV winding | kV rms | 3 |  |
|  | Rated lightning impulse withstand voltage (1.2/50 µs) |  |  |  |
|  | HV winding | kV peak | 125 |  |
|  | Impedance voltage in % at 75°C, full load — HV-LV | % | 4 |  |
|  | Tolerances for penalty / rejection | IEC | 60076-1 |  |
|  | No load losses at nominal voltage | kW | 0.45 |  |
|  | Load losses at 75°C and full load position | kW | 2.5 |  |
|  | Creepage distance | mm/kV | 31.5 |  |
|  | Off load tap changer — tappings and ration | % | +/-5, +/-2x2.5 |  |
|  | Noise level | dBA | <60 |  |
|  | Accessories |  |  |  |
|  | Sealed transformer |  | yes |  |
|  | Oil thermometer sensor with two contacts |  | as required |  |
|  | Winding thermometer sensors with two contacts |  | as required |  |
|  | Pressure relieve device / Name plate / Connection diagram |  | yes |  |
|  | Designation plate for all devices / Tap position indicator |  | yes |  |
|  | Test Requirements — Standard applied: IEC 60076-1 |  |  |  |
|  | Type tests |  |  |  |
|  | Temperature rise test (IEC 60076-2 Clause 5.2.3) |  | yes |  |
|  | Noise level (IEC 60076-10) |  | yes |  |
|  | Routine tests |  |  |  |
|  | Measurement of DC resistance (Clause 11.2) |  | yes |  |
|  | Measuring of voltage ratio and phase displacement (Clause 11.3) |  | yes |  |
|  | Measuring of short circuit impedance and load losses (Clause 11.4) |  | yes |  |
|  | Measuring of no-load losses and current (Clause 11.5) |  | yes |  |
|  | Dielectric routine tests |  |  |  |
|  | Lightning impulse withstand test (Clause 13 & 14) |  | yes |  |
|  | Long duration induced AC voltage tests (Clause 12.4) |  | yes |  |
|  | Separate source AC voltage test (Clause 11) |  | yes |  |
|  | Auxiliary wiring test (Clause 10) |  | yes |  |

### Diesel Generator

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | Power transformers, auxiliary transformers and diesel generator |  |  |  |
|  | Diesel generator |  |  |  |
|  | Applicable standard | ISO | 8528-1 to 5 |  |
|  | Type |  | Standby |  |
|  | Location of installation |  | fixed, Generator Canopy |  |
|  | Engine |  |  |  |
|  | Type |  | Diesel |  |
|  | Rated speed | rpm | By Bidder |  |
|  | Rated power at rated speed | kW | 100 |  |
|  | Type of cooling / lubrication / exhaust / governor / frequency regulation |  | By Bidder |  |
|  | Capacity of day tank | liters | By Bidder |  |
|  | Accessories |  |  |  |
|  | Name plate / Connection diagram / Designation plate for all devices |  | yes |  |
|  | Fixation |  | Base frame with the generator |  |
|  | Generator |  |  |  |
|  | Number of phases | # | 3 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Rated Voltage | V | 400/230 |  |
|  | Rated power | kVA | 125 |  |
|  | Exciter type |  | brushless |  |
|  | Accessories / Controls / Monitoring |  | As specified |  |
|  | Test requirements |  |  |  |
|  | Applicable standard | ISO | 8528-6 |  |

## D. 20 kV Switchyard Equipment (MV Equipment)

### 20 kV Switchgear for Auxiliary Supply and Distribution

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | MV Equipment |  |  |  |
|  | 20 kV switchgears for auxiliary supply and distribution |  |  |  |
|  | Applicable standard | IEC | 62271-200, 60694 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Type of switchgear | - | Indoor |  |
|  | Number of phases | # | 3 |  |
|  | Number of bus bars | # | 1 |  |
|  | Nominal voltage | kV | 20 |  |
|  | Rated voltage | kV | 24 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Rated power frequency withstand voltage | kV rms | 50 |  |
|  | Rated lightning impulse withstand voltage (1.2/50 µs) | kV peak | 125 |  |
|  | Rated short-time current, 3s | kA | 25 |  |
|  | Rated peak withstand current | kA | 62.5 |  |
|  | Rated current for busbar | A | 1600 |  |
|  | Rated current for distribution and incomer feeders | A | 630, 1250 |  |
|  | Feeder for auxiliary transformers | A | 630 |  |
|  | Type of drive |  | spring, wound-up by electric motor or manual |  |
|  | Power supply for drive / auxiliary contacts | V | 220 DC |  |
|  | Power supply for heaters | VAC | 230 |  |
|  | Circuit breaker |  |  |  |
|  | Applicable standard | IEC | 62271-100 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Type |  | Vacuum |  |
|  | Rated current busbar | A | 1600 |  |
|  | Rated current feeders | A | 630, 1250 |  |
|  | Rated current auxiliary supply | A | 630 |  |
|  | Rated short-time current, 3s | kA | 25 |  |
|  | Rated short circuit current | kA | 62.5 |  |
|  | Rated operating sequence (three-phase auto reclosing) | - | 0-0.3s-CO-3min-CO |  |
|  | Maximum breaking time | ms | 60 |  |
|  | Maximum making time | ms | 100 |  |
|  | Number of tripping coils |  | 2 |  |
|  | Number of closing coils |  | 1 |  |
|  | Protection class | - | IP 54 |  |
|  | Auto-reclosing |  | three phase |  |
|  | Drive | - | 3 pole |  |
|  | Type of drive | - | spring, wound-up by electric motor or manual |  |
|  | Power supply for drive / auxiliary contacts | V | 220 DC |  |
|  | Power supply for heaters | VAC | 230 |  |
|  | Earthing switch |  |  |  |
|  | Rated current | A | 1250 |  |
|  | Rated short time current | kA | 25 |  |
|  | Rated peak withstand current | kA | 62.5 |  |
|  | Current transformer |  |  |  |
|  | Rated primary current for income | A | 1250 |  |
|  | Rated primary current for outgoing | A | 630 |  |
|  | Secondary currents | A | 1 |  |
|  | Number of secondary windings | # | 3 |  |
|  | Accuracy class |  | 0.5M5/0.2 M2/5P20 PX, 0.5 |  |
|  | Voltage transformers |  |  |  |
|  | Primary voltage | kV | 20/√3 |  |
|  | Secondary voltage |  | 110√3, 110/3 |  |
|  | Number of windings | # | 3 |  |
|  | Accuracy class | % | 0.2/3P |  |
|  | Type of metal enclosed switchgear |  | LSC2A |  |
|  | Class of partitions and shutters |  | PM |  |
|  | IAC classification required for It (3 sec) | kA | 25 |  |
|  | IAC classification required for Ip | kA | 62.5 |  |
|  | IAC classification required for |  | F |  |
|  | Test Requirements — Standard applied: IEC 62271-200, IEC 60694 |  |  |  |
|  | Mandatory Type tests |  |  |  |
|  | Verification of insulation level (Clause 6.2) |  | yes |  |
|  | Measuring of resistance of main contacts (Clause 6.4) |  | yes |  |
|  | Temperature rise test (Clause 6.5) |  | yes |  |
|  | Short time withstand current and peak withstand current test for main circuit and earthing switch (Clause 6.6) |  | yes |  |
|  | Test to proof making and breaking capacity of switching devices (Clause 6.101) |  | yes |  |
|  | Mechanical operation tests of the switching devices (Clause 6.102) |  | yes |  |
|  | Test to verify protection of persons against access to hazardous parts / foreign objects (Clause 6.7) |  | yes |  |
|  | Test to verify protection of persons against dangerous electrical effects (Clause 6.104) |  | yes |  |
|  | Tests to assess effects of arcing due to internal faults (Clause 6.106) |  | yes |  |
|  | Electromagnetic compatibility test (Clause 6.9) |  | yes |  |
|  | Routine tests |  |  |  |
|  | Dielectric tests on main circuit (Clause 7.1, IEC 60694) |  | yes |  |
|  | Tests on auxiliary and control circuits (Clause 7.2, IEC 60694 and Clause 7.104) |  | yes |  |
|  | Measurement of resistance of main contacts (Clause 7.3, IEC 60694) |  | yes |  |
|  | Design and visual check (Clause 7.5, IEC 60694) |  | yes |  |
|  | Mechanical operations tests (IEC 62271-200 Clause 7.102) |  | yes |  |
|  | Tests after erection on site (IEC 62271-200 Clause 7.105) |  | yes |  |

## E. MV, LV Power Cables, Control Cables and Cable Trays

### MV Power Cables

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | MV, LV power cables, control cables and cable trays |  |  |  |
|  | MV power cables |  |  |  |
|  | Applicable standard | IEC | 60502 part 2 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Type of cable |  | Single core |  |
|  | Insulation material |  | XLPE |  |
|  | Rated voltage Uo/U | kV | 12/20 |  |
|  | Highest voltage | kV | 24 |  |
|  | Category of cable |  | A |  |
|  | Maximum conductor temperature normal operation | °C | 90 |  |
|  | Maximum conductor temperature after short circuit | °C | 250 |  |
|  | Conductor material |  | copper |  |
|  | Nominal thickness of insulation at rated voltage | mm | 5.5 |  |
|  | Accessories — Cable termination |  |  |  |
|  | Applicable standard | IEC | 60502 |  |
|  | Type |  | single-core, one-piece insulator, push-on type |  |
|  | Insulation material |  | silicone rubber or porcelain |  |
|  | Conductor connection |  | compression type |  |
|  | Test requirements — Applied standard: IEC 60502 |  |  |  |
|  | Routine tests on manufactured length |  |  |  |
|  | Measurement of resistance of conductor (Clause 16.2) |  | yes |  |
|  | Partial discharge test (Clause 16.3) |  | yes |  |
|  | Voltage test (Clause 16.4) |  | yes |  |
|  | Sample tests |  |  |  |
|  | Conductor examination (Clause 17.4) |  | yes |  |
|  | Check of dimensions (Clause 17.5 to 17.8) |  | yes |  |
|  | Voltage test (Clause 17.9) |  | yes |  |
|  | Hot set test (Clause 17.10) |  | yes |  |
|  | Type tests |  |  |  |
|  | Partial discharge test (Clause 18.1.3) |  | yes |  |
|  | Bending tests followed by partial discharge tests (Clause 18.1.4) |  | yes |  |
|  | Tan δ measurement (Clause 18.1.2 and 18.1.5) |  | yes |  |
|  | Heat cycle voltage tests followed by partial discharge test (Clause 18.1.6) |  | yes |  |
|  | Impulse voltage test followed by voltage test (Clause 18.1.7) |  | yes |  |
|  | Voltage test for 4 hours (Clause 18.1.8) |  | yes |  |

### LV Power Cables (0.4 kV) — Single, Three & Four Core

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV, MV, LV power cables, control cables and cable trays |  |  |  |
|  | 0.4 kV LV power cables (single / three / four core) |  |  |  |
|  | Applied standard | IEC | 60502-1 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Insulation material |  | PVC |  |
|  | Rated voltage Uo/U | kV | 0.6/1 |  |
|  | Highest voltage | kV | 1.2 |  |
|  | Category of cable |  | A |  |
|  | Maximum conductor temperature normal operation | °C | 70 |  |
|  | Maximum conductor temperature after short circuit | °C | 160 |  |
|  | Conductor material |  | copper |  |
|  | Cable termination — Standard applied | IEC | 60502-1 |  |

### 0.4 kV Control Cables

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV, MV, LV power cables, control cables and cable trays |  |  |  |
|  | 0.4 kV control cables |  |  |  |
|  | Applied standard | IEC | 60502-1 |  |
|  | Manufacturer |  | By Bidder |  |
|  | Insulation material |  | PVC |  |
|  | Rated voltage Uo/U | kV | 0.6/1 |  |
|  | Highest voltage | kV | 1.2 |  |
|  | Category of cable |  | B |  |
|  | Maximum conductor temperature normal operation | °C | 70 |  |
|  | Maximum conductor temperature after short circuit | °C | 160 |  |
|  | Conductor material |  | copper |  |
|  | Test requirements — Applied standard: IEC 60502-1, 2011 |  |  |  |
|  | Routine tests |  |  |  |
|  | Measurement of resistance of conductor (Clause 15.2) |  | yes |  |
|  | Voltage test (Clause 15.3) |  | yes |  |
|  | Sample tests |  |  |  |
|  | Conductor examination (Clause 16.4) |  | yes |  |
|  | Check of dimensions (Clause 16.5 to 16.8) |  | yes |  |
|  | Type tests |  |  |  |
|  | Insulation resistance at ambient temperature (Clause 17.1) |  | yes |  |
|  | Insulation resistance at maximum conductor temperature (Clause 17.2) |  | yes |  |
|  | Voltage test for 4 hours (Clause 17.3) |  | yes |  |

### DC Cables

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV, MV, LV power cables, control cables and cable trays |  |  |  |
|  | DC cables |  |  |  |
|  | Applied standard | IEC | 60502-1 |  |
|  | Insulation material |  | PVC |  |
|  | Rated voltage Uo/U | kV | 0.6/1 |  |
|  | Highest voltage | kV | 1.2 |  |
|  | Category of cable |  | B |  |
|  | Maximum conductor temperature normal operation | °C | 70 |  |
|  | Maximum conductor temperature after short circuit | °C | 160 |  |
|  | Conductor material |  | copper |  |
|  | Test requirements — same regime as 0.4 kV control cables (IEC 60502-1) |  |  |  |

### Lighting Cables and Heat-Resistant Cables

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV, MV, LV power cables, control cables and cable trays |  |  |  |
|  | Lighting cables |  |  |  |
|  | Applied standard | IEC | 60227 |  |
|  | Insulation material |  | PVC |  |
|  | Rated voltage Uo/U | kV | 0.45/0.75 |  |
|  | Highest voltage | kV | 0.75 |  |
|  | Category of cable |  | B |  |
|  | Conductor material |  | copper |  |
|  | Test requirements — Applied standard | IEC | 60227-2 |  |
|  | Heat resistant cables |  |  |  |
|  | Rated voltage Uo/U | kV | 0.6/1 |  |
|  | Highest voltage | kV | 1.2 |  |
|  | Ambient temperature | °C | 60 |  |
|  | Max conductor temperature | °C | 180 |  |
|  | Test requirements |  | To be defined by the Bidder |  |

### Cable Trays

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | HV, MV, LV power cables, control cables and cable trays |  |  |  |
|  | Cable trays |  |  |  |
|  | Material |  | steel |  |
|  | Corrosion protection |  | Hot deep galvanization |  |
|  | Thickness of galvanization | µm | ≥100 |  |
|  | Test requirements |  |  |  |
|  | Visual inspection |  | yes |  |
|  | Galvanization test |  | yes |  |

## F. AC/DC Installations

### 0.4 kV Switchgear

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | AC DC Installations |  |  |  |
|  | 0.4 kV switchgear |  |  |  |
|  | Applicable standard | IEC | 61439-1 and 2 |  |
|  | Type of switchgear | - | Indoor |  |
|  | Number of phases | # | 3 |  |
|  | Number of bus bars | # | 1 |  |
|  | Nominal voltage | kV | 0.4 |  |
|  | Rated voltage | kV | 1 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Rated short-time current, 3s | kA | 10 |  |
|  | Rated peak withstand current | kA | 25 |  |
|  | Rated current for busbar | A | 450 |  |
|  | Rated current for distribution feeders | A | 300 |  |
|  | Type of drive |  | spring, wound-up by electric motor or manual |  |
|  | Power supply for drive / auxiliary contacts | V | 220 DC |  |
|  | Power supply for heaters | VAC | 230 |  |
|  | Current transformer |  |  |  |
|  | Rated primary current | A | 450 |  |
|  | Secondary currents | A | 1 |  |
|  | Number of secondary windings | # | 2 |  |
|  | Accuracy class |  | 1.5M5/10P10 |  |
|  | Test Requirements — Standard applied: IEC 61439-1,2 |  |  |  |
|  | Verifying tests |  |  |  |
|  | Strength of material and parts (Clause 10.2) |  | yes |  |
|  | Verification of the degree of protection of the enclosure (Clause 10.3) |  | yes |  |
|  | Verification of creepage distances (Clause 10.4) |  | yes |  |
|  | Effective continuity between parts and PE (Clause 10.5.2) |  | yes |  |
|  | Effectiveness of the assembly for external faults (Clause 10.5.3) |  | yes |  |
|  | Power frequency withstand voltage test (Clause 10.9.2) |  | yes |  |
|  | Impulse withstand voltage test (Clause 10.9.3) |  | yes |  |
|  | Temperature rise test (Clause 10.10) |  | yes |  |
|  | Short circuit withstand test (Clause 10.11) |  | yes |  |
|  | Electromagnetic compatibility test (Clause 10.12) |  | yes |  |
|  | Mechanical operation tests (Clause 10.13) |  | yes |  |
|  | Routine verifying tests |  |  |  |
|  | Dielectric tests on main circuit |  | yes |  |
|  | Tests on auxiliary and control circuits |  | yes |  |
|  | Design and visual check |  | yes |  |
|  | Mechanical operations tests |  | yes |  |

### DC Distribution Panels

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | AC DC Installations |  |  |  |
|  | DC distribution panels |  |  |  |
|  | Applicable standard | IEC | 61439-1 and 2 |  |
|  | Type of switchgear | - | Indoor |  |
|  | Number of phases | # | 2 |  |
|  | Number of bus bars | # | 1 |  |
|  | Nominal voltage | DCV | 220 |  |
|  | Rated power frequency withstand voltage | kV rms | 2.5 |  |
|  | Rated short-time current, 3s | kA | 6 |  |
|  | Rated peak withstand current | kA | 15 |  |
|  | Power supply for heaters | VAC | 230 |  |
|  | Insulation resistance | mOhm | 125 |  |
|  | Test Requirements — same verifying/routine tests as 0.4 kV switchgear above (IEC 61439-1,2) |  |  |  |

### Battery Chargers (220V DC and 48V DC)

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | AC DC Installations |  |  |  |
|  | 220V DC Battery chargers |  |  |  |
|  | Applicable standard | IEC | 60146 |  |
|  | Type |  | indoor |  |
|  | Type of controls |  | thyristor control |  |
|  | Type of cooling |  | Self-ventilating |  |
|  | Rated voltage primary | V | 400 |  |
|  | Rated voltage secondary | DCV | 220 +/- 20% |  |
|  | IP protection | IP | 52 |  |
|  | Mounted in metal cabinet |  | yes |  |
|  | 48 V battery charger |  |  |  |
|  | Applicable standard | IEC | 60146 |  |
|  | Type |  | indoor |  |
|  | Type of controls |  | thyristor control |  |
|  | Rated voltage primary | V | 400/230 |  |
|  | Rated voltage secondary | DCV | 48 +/- 20% |  |
|  | IP protection | IP | 52 |  |
|  | Mounted in metal cabinet |  | yes |  |

### Batteries (220V DC and 48V DC)

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | AC DC Installations |  |  |  |
|  | 220V DC Batteries |  |  |  |
|  | Applicable standard | IEC | 60086-1 |  |
|  | Type |  | lead acid sealed |  |
|  | Installed on wooden rack |  | yes |  |
|  | Set of maintenance tools |  | yes |  |
|  | 48 VDC Batteries |  |  |  |
|  | Applicable standard | IEC | 60086-1 |  |
|  | Type |  | lead acid sealed |  |
|  | Voltage per cell | VDC | 2 |  |
|  | Installed on wooden rack |  | yes |  |
|  | Set of maintenance tools |  | yes |  |

## G. Lighting and Small Power Installations

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | Lighting and small power installations |  |  |  |
|  | Lighting installation |  |  |  |
|  | Applied standards | IEC | 60968, 60969, 62560, 62612 |  |
|  | Sub-distribution boards |  | according to specs |  |
|  | Illumination |  | according to the specs |  |
|  | Emergency lighting |  |  |  |
|  | Operation voltage | VDC | 220 |  |
|  | Lighting intensity | Lux | 50 |  |
|  | Outdoor lighting |  |  |  |
|  | Lighting intensity | Lux | 14 |  |
|  | Fence lighting |  | yes |  |
|  | Test requirements |  |  |  |
|  | Measurement of lighting intensity after installation for normal, emergency and outdoor lighting |  | yes |  |
|  | Small power installation |  |  |  |
|  | Requirement according to Specs |  | yes |  |
|  | Domestic outlets according to Specification |  | yes |  |
|  | Visual inspection after installation |  | yes |  |

## H. Earthing and Lightning Protection Systems

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | Earthing and lightning protection systems |  |  |  |
|  | Earthing system |  |  |  |
|  | Applied standard | IEEE / IEC | 80 / 60621 |  |
|  | Calculation of the length of the earthing mesh conductor | IEEE | 80 |  |
|  | Calculation of step voltage | IEEE | 80 |  |
|  | Calculation of touch voltages | IEEE | 80 |  |
|  | Material for electrodes |  | stranded copper conductor |  |
|  | Minimum cross section of the grid conductor | mm2 | 120 |  |
|  | Mode of connection of copper conductor in the ground |  | compression or thermo weld |  |
|  | Material for fixing the earthing conductor clamps |  | by compression |  |
|  | Material of clamps for earthing conductor connections |  | tinned copper |  |
|  | Material for bolts and nuts |  | galvanized steel |  |
|  | Method of connecting the earthing conductor to the steel structure |  | bolts, nut, washers and lock washers |  |
|  | Minimum dept of conductor burring | m | 0.8 |  |
|  | Earthing resistance of the complete substation | Ω | ≤0.5 |  |
|  | Test requirements |  |  |  |
|  | Measurement of earthing resistance after installation |  | yes |  |
|  | Measurement of earthing resistance before commissioning |  | yes |  |
|  | Lightning protection system |  |  |  |
|  | Applied standard | IEC / VDE | 62305 / 185 |  |
|  | Design |  | Rolling sphere principle |  |
|  | Material |  | Steel rods |  |
|  | Cross section | mm2 | 50 |  |
|  | System coverage |  | whole substation area |  |
|  | The system to comply with the specification |  | yes |  |
|  | Test requirements |  |  |  |
|  | Visual inspection after installation |  | yes |  |
|  | Continuity tests after installation |  | yes |  |

## I. Protection and Control

| Item No. | Schedule of Technical Data | Unit | Required | Offered Data |
| --- | --- | --- | --- | --- |
|  | Protection and Control |  |  |  |
|  | General |  |  |  |
|  | Relays | - | Numerical |  |
|  | Latest standard of | - | IEC 60255 |  |
|  | Maximum ambient temperature for rated accuracy | °C | 40 |  |
|  | Maximum temperature by storage | °C | 60 |  |
|  | Maximum humidity | % | 80 |  |
|  | Electromagnetic compatibility tests | - | EN 50081, EN 50082-1, IEC 60255-6 |  |
|  | Insulation tests | - | IEC 60255-5, IEC 60870-2-1 |  |
|  | Mechanical tests (vibration and shock stress) | - | IEC 60255-2-1, IEC 60068-2 |  |
|  | Other: all other norms as specified on technical document | - | IEC |  |
|  | Protection functions to be provided for 220 kV feeders, transformers, and 20 kV feeders |  | By Bidder, as per single line diagram and protection philosophy |  |
|  | SCADA / RTU integration and communication protocol |  | IEC 60870-5-104 / IEC 61850, as specified |  |
|  | Metering system |  | revenue-grade, Class 0.2S, as specified |  |